## Master Table
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | input 7 | input 8 | dropdown 1 | dropdown 2 | dropdown 3 | dropdown 4 | dropdown 5 | dropdown 6 | dropdown 7 | dropdown 8 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | # pieces | n, free area ratio | curve ratio, CR | splitter vanes | configuration | R (in) | S (in) | t/D | h/D | y/D or y/H | L/D | R/D | L/R | W₁/W | L/W | R/W | H/W | W/H | L/H | h/H | S_m/A | A/A1 | A1/A | As/A | Ah/A | As/Ah | Ab/Ac | As/Ac | Ab/As | A_1b/Ac or A_2b/Ac | Vc | Vb/Vc | Vs/Vc | V_1b/Vc or V_2b/Vc | V/V0 | V, fpm | V, m/s | Qb/Qc | Qb/Qs | Qs/Qc | Q_1b/Qc or Q_2b/Qc | Re | R_e | ANGLE | K_ANGLE | K | C
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) |  | D (in) | R/D - select from list | θ (degrees) | Q (cfm) | N/A | N/A | N/A | N/A |  | 1 | 0 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [11 empty] | 0.5 | [31 empty] | 0 |  | 0 | 0.71
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) |  | D (mm) | R/D - select from list | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A | N/A |  | 1.5 | 20 | [26 empty] | 0.75 | [31 empty] | 20 |  | 0.31 | 0.33
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 30 | [26 empty] | 1 | [31 empty] | 30 |  | 0.45 | 0.22
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 45 | [26 empty] | 1.5 | [31 empty] | 45 |  | 0.6 | 0.15
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 60 | [26 empty] | 2 | [31 empty] | 60 |  | 0.78 | 0.13
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 75 | [26 empty] | 2.5 | [31 empty] | 75 |  | 0.9 | 0.12
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 90 | [58 empty] | 90 |  | 1
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 110 | [58 empty] | 110 |  | 1.13
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 130 | [58 empty] | 130 |  | 1.2
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 150 | [58 empty] | 150 |  | 1.28
A7A | A-7 | Elbow | A | Round | Smooth Radius (Die Stamped) | [11 empty] | 180 | [58 empty] | 180 |  | 1.4
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° |  | D (in) | R/D - select from list | # pieces - select from list | Q (cfm) | N/A | N/A | N/A | N/A |  | 1 | 3 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | 3 | [10 empty] | 0.5 | [34 empty] | 0.98
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° |  | D (mm) | R/D - select from list | # pieces - select from list | Q (m^3/hr) | N/A | N/A | N/A | N/A |  | 1.5 | 4 | [15 empty] | 3 | [10 empty] | 0.75 | [34 empty] | 0.54
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [11 empty] | 5 | [15 empty] | 3 | [10 empty] | 1 | [34 empty] | 0.42
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 3 | [10 empty] | 1.5 | [34 empty] | 0.34
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 3 | [10 empty] | 2 | [34 empty] | 0.33
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 4 | [10 empty] | 0.75 | [34 empty] | 0.5
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 4 | [10 empty] | 1 | [34 empty] | 0.37
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 4 | [10 empty] | 1.5 | [34 empty] | 0.27
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 4 | [10 empty] | 2 | [34 empty] | 0.24
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 5 | [10 empty] | 0.75 | [34 empty] | 0.46
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 5 | [10 empty] | 1 | [34 empty] | 0.33
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 5 | [10 empty] | 1.5 | [34 empty] | 0.24
A7B | A-7 | Elbow | B | Round | 3-to 5 Piece, 90° | [27 empty] | 5 | [10 empty] | 2 | [34 empty] | 0.19
A7C | A-7 | Elbow | C | Round | Mitered Round |  | D (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A | N/A | N/A |  | 20 | [6 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [43 empty] | 20 |  |  | 0.08
A7C | A-7 | Elbow | C | Round | Mitered Round |  | D (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A | N/A | N/A |  | 30 | [59 empty] | 30 |  |  | 0.16
A7C | A-7 | Elbow | C | Round | Mitered Round | [10 empty] | 45 | [59 empty] | 45 |  |  | 0.34
A7C | A-7 | Elbow | C | Round | Mitered Round | [10 empty] | 60 | [59 empty] | 60 |  |  | 0.55
A7C | A-7 | Elbow | C | Round | Mitered Round | [10 empty] | 75 | [59 empty] | 75 |  |  | 0.81
A7C | A-7 | Elbow | C | Round | Mitered Round | [10 empty] | 90 | [59 empty] | 90 |  |  | 1.2
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular |  | H (in) | W (in) | θ (degrees) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [16 empty] | 0.25 | [26 empty] | 20 |  |  | 0.08
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular |  | H (mm) | W (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [34 empty] | 0.25 | [26 empty] | 30 |  |  | 0.18
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.25 | [26 empty] | 45 |  |  | 0.38
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.25 | [26 empty] | 60 |  |  | 0.6
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.25 | [26 empty] | 75 |  |  | 0.89
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.25 | [26 empty] | 90 |  |  | 1.3
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 20 |  |  | 0.08
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 30 |  |  | 0.17
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 45 |  |  | 0.37
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 60 |  |  | 0.59
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 75 |  |  | 0.87
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.5 | [26 empty] | 90 |  |  | 1.3
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 20 |  |  | 0.08
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 30 |  |  | 0.17
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 45 |  |  | 0.36
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 60 |  |  | 0.57
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 75 |  |  | 0.84
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 0.75 | [26 empty] | 90 |  |  | 1.2
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 20 |  |  | 0.07
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 30 |  |  | 0.16
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 45 |  |  | 0.34
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 60 |  |  | 0.55
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 75 |  |  | 0.81
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1 | [26 empty] | 90 |  |  | 1.2
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 20 |  |  | 0.07
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 30 |  |  | 0.15
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 45 |  |  | 0.33
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 60 |  |  | 0.52
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 75 |  |  | 0.77
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 1.5 | [26 empty] | 90 |  |  | 1.1
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 20 |  |  | 0.07
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 30 |  |  | 0.15
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 45 |  |  | 0.31
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 60 |  |  | 0.49
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 75 |  |  | 0.73
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 2 | [26 empty] | 90 |  |  | 1.1
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 20 |  |  | 0.06
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 30 |  |  | 0.13
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 45 |  |  | 0.27
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 60 |  |  | 0.43
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 75 |  |  | 0.63
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 4 | [26 empty] | 90 |  |  | 0.92
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 20 |  |  | 0.05
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 30 |  |  | 0.12
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 45 |  |  | 0.25
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 60 |  |  | 0.39
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 75 |  |  | 0.58
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 6 | [26 empty] | 90 |  |  | 0.85
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 20 |  |  | 0.05
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 30 |  |  | 0.11
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 45 |  |  | 0.24
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 60 |  |  | 0.38
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 75 |  |  | 0.57
A7D | A-7 | Elbow | D | Rectangular | Mitered Rectangular | [43 empty] | 8 | [26 empty] | 90 |  |  | 0.83
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow |  | W₁ (in) | W (in) | H (in) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [13 empty] | 0.6 |  |  | 0.25 | [29 empty] | 1.8
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow |  | W₁ (mm) | W (mm) | H (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [31 empty] | 0.8 |  |  | 0.25 | [29 empty] | 1.4
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.2 |  |  | 0.25 | [29 empty] | 1.1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.4 |  |  | 0.25 | [29 empty] | 1.1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.6 |  |  | 0.25 | [29 empty] | 1.1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 2 |  |  | 0.25 | [29 empty] | 1.1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.6 |  |  | 1 | [29 empty] | 1.7
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.8 |  |  | 1 | [29 empty] | 1.1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.2 |  |  | 1 | [29 empty] | 1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.4 |  |  | 1 | [29 empty] | 0.95
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.6 |  |  | 1 | [29 empty] | 0.9
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 2 |  |  | 1 | [29 empty] | 0.84
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.6 |  |  | 4 | [29 empty] | 1.5
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.8 |  |  | 4 | [29 empty] | 1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.2 |  |  | 4 | [29 empty] | 0.81
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.4 |  |  | 4 | [29 empty] | 0.76
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.6 |  |  | 4 | [29 empty] | 0.72
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 2 |  |  | 4 | [29 empty] | 0.66
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.6 |  |  | 8 | [29 empty] | 1.5
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 0.8 |  |  | 8 | [29 empty] | 1
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.2 |  |  | 8 | [29 empty] | 0.69
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.4 |  |  | 8 | [29 empty] | 0.63
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 1.6 |  |  | 8 | [29 empty] | 0.6
A7E | A-7 | Elbow | E | Rectangular | Mitered, with Converging/Diverging Flow | [40 empty] | 2 |  |  | 8 | [29 empty] | 0.55
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° |  | H (in) | W (in) | R (in) | θ (degrees) | Q (cfm) | N/A | N/A | N/A |  |  |  | 30 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [15 empty] | 0.5 | 0.25 | [24 empty] | 10000 |  |  |  | 1.4 | 1.5
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° |  | H (mm) | W (mm) | R (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 45 | [29 empty] | 0.75 | 0.25 | [24 empty] | 20000 |  |  |  | 1.26 | 0.57
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [12 empty] | 60 | [29 empty] | 1 | 0.25 | [24 empty] | 30000 |  |  |  | 1.19 | 0.27
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [12 empty] | 75 | [29 empty] | 1.5 | 0.25 | [24 empty] | 40000 |  |  |  | 1.14 | 0.22
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [12 empty] | 90 | [29 empty] | 2 | 0.25 | [24 empty] | 60000 |  |  |  | 1.09 | 0.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 0.5 | [24 empty] | 80000 |  |  |  | 1.06 | 1.4
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 0.5 | [24 empty] | 100000 |  |  |  | 1.04 | 0.52
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 0.5 | [24 empty] | 140000 |  |  |  | 1 | 0.25
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 0.5 | [24 empty] | 200000 |  |  |  | 1 | 0.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 0.5 | [24 empty] | 10000 |  |  |  | 2 | 0.18
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 0.75 | [24 empty] | 20000 |  |  |  | 1.77 | 1.3
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 0.75 | [24 empty] | 30000 |  |  |  | 1.64 | 0.48
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 0.75 | [24 empty] | 40000 |  |  |  | 1.56 | 0.23
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 0.75 | [24 empty] | 60000 |  |  |  | 1.46 | 0.19
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 0.75 | [24 empty] | 80000 |  |  |  | 1.38 | 0.16
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 1 | [24 empty] | 100000 |  |  |  | 1.3 | 1.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 1 | [24 empty] | 140000 |  |  |  | 1.15 | 0.44
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 1 | [24 empty] | 200000 |  |  |  | 1 | 0.21
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 1 | [29 empty] | 0.17
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 1 | [29 empty] | 0.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 1.5 | [29 empty] | 1.1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 1.5 | [29 empty] | 0.4
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 1.5 | [29 empty] | 0.19
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 1.5 | [29 empty] | 0.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 1.5 | [29 empty] | 0.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 2 | [29 empty] | 1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 2 | [29 empty] | 0.39
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 2 | [29 empty] | 0.18
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 2 | [29 empty] | 0.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 2 | [29 empty] | 0.13
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 3 | [29 empty] | 1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 3 | [29 empty] | 0.39
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 3 | [29 empty] | 0.18
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 3 | [29 empty] | 0.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 3 | [29 empty] | 0.13
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 4 | [29 empty] | 1.1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 4 | [29 empty] | 0.4
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 4 | [29 empty] | 0.19
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 4 | [29 empty] | 0.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 4 | [29 empty] | 0.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 5 | [29 empty] | 1.1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 5 | [29 empty] | 0.42
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 5 | [29 empty] | 0.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 5 | [29 empty] | 0.16
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 5 | [29 empty] | 0.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 6 | [29 empty] | 1.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 6 | [29 empty] | 0.43
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 6 | [29 empty] | 0.27
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 6 | [29 empty] | 0.17
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 6 | [29 empty] | 0.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.5 | 8 | [29 empty] | 1.2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 0.75 | 8 | [29 empty] | 0.44
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1 | 8 | [29 empty] | 0.21
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 1.5 | 8 | [29 empty] | 0.17
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | 2 | 8 | [29 empty] | 0.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 10000 |  |  | 1.4
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 20000 |  |  | 1.26
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 30000 |  |  | 1.19
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 40000 |  |  | 1.14
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 60000 |  |  | 1.09
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 80000 |  |  | 1.06
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 100000 |  |  | 1.04
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | 140000 |  |  | 1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | <0.5 | [26 empty] | >=200000 |  |  | 1
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 10000 |  |  | 2
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 20000 |  |  | 1.77
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 30000 |  |  | 1.64
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 40000 |  |  | 1.56
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 60000 |  |  | 1.46
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 80000 |  |  | 1.38
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 100000 |  |  | 1.3
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | 140000 |  |  | 1.15
A7F | A-7 | Elbow | F | Rectangular | Smooth Radius without Vanes, 90° | [42 empty] | >=0.75 | [26 empty] | >=200000 |  |  | 1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes |  | H (in) | W (in) | centerline radius (in) | # vanes - select from list | θ (degrees) | Q (cfm) | N/A | N/A |  |  |  | 1 | 30 |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  |  | 0.218 | 1 | [11 empty] | 0.05 | 0.25 | [24 empty] | 10000 |  |  |  | 1.4 | 0.52
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes |  | H (mm) | W (mm) | centerline radius (mm) | # vanes - select from list | θ (degrees) | Q (m^3/hr) | N/A | N/A |  |  |  | 2 | 45 | [15 empty] | 0.302 | 1 | [11 empty] | 0.1 | 0.25 | [24 empty] | 20000 |  |  |  | 1.26 | 0.36
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 3 | 60 | [15 empty] | 0.361 | 1 | [11 empty] | 0.15 | 0.25 | [24 empty] | 30000 |  |  |  | 1.19 | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [13 empty] | 75 | [15 empty] | 0.408 | 1 | [11 empty] | 0.2 | 0.25 | [24 empty] | 40000 |  |  |  | 1.14 | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [13 empty] | 90 | [15 empty] | 0.447 | 1 | [11 empty] | 0.25 | 0.25 | [24 empty] | 60000 |  |  |  | 1.09 | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 0.25 | [24 empty] | 80000 |  |  |  | 1.06 | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 0.25 | [24 empty] | 100000 |  |  |  | 1.04 | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 0.25 | [24 empty] | 140000 |  |  |  | 1 | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 0.25 | [24 empty] | 200000 |  |  |  | 1 | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 0.25 | [24 empty] | 10000 |  |  |  | 2 | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 0.25 | [24 empty] | 20000 |  |  |  | 1.77 | 0.26
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 0.25 | [24 empty] | 30000 |  |  |  | 1.64 | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 0.25 | [24 empty] | 40000 |  |  |  | 1.56 | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 0.25 | [24 empty] | 60000 |  |  |  | 1.46 | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 0.25 | [24 empty] | 80000 |  |  |  | 1.38 | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 0.25 | [24 empty] | 100000 |  |  |  | 1.3 | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 0.25 | [24 empty] | 140000 |  |  |  | 1.15 | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 0.25 | [24 empty] | 200000 |  |  |  | 1 | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 0.25 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 0.25 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 0.25 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 0.25 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 0.25 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 0.25 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 0.25 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 0.25 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 0.25 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 0.25 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 0.25 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 0.25 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 0.5 | [29 empty] | 0.4
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 0.5 | [29 empty] | 0.27
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 0.5 | [29 empty] | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 0.5 | [29 empty] | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 0.5 | [29 empty] | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 0.5 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 0.5 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 0.5 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 0.5 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 0.5 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 0.5 | [29 empty] | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 0.5 | [29 empty] | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 0.5 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 0.5 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 0.5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 0.5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 0.5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 0.5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 0.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 0.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 0.5 | [29 empty] | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 0.5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 0.5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 0.5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 0.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 0.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 0.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 0.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 0.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 0.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 1 | [29 empty] | 0.43
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 1 | [29 empty] | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 1 | [29 empty] | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 1 | [29 empty] | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 1 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 1 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 1 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 1 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 1 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 1 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 1 | [29 empty] | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 1 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 1 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 1 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 1 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 1 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 1 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 1 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 1 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 1 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 1 | [29 empty] | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 1 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 1 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 1 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 1 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 1 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 1 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 1 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 1 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 1 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 1.5 | [29 empty] | 0.49
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 1.5 | [29 empty] | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 1.5 | [29 empty] | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 1.5 | [29 empty] | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 1.5 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 1.5 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 1.5 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 1.5 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 1.5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 1.5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 1.5 | [29 empty] | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 1.5 | [29 empty] | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 1.5 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 1.5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 1.5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 1.5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 1.5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 1.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 1.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 1.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 1.5 | [29 empty] | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 1.5 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 1.5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 1.5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 1.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 1.5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 1.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 1.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 1.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 1.5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 2 | [29 empty] | 0.55
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 2 | [29 empty] | 0.3
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 2 | [29 empty] | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 2 | [29 empty] | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 2 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 2 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 2 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 2 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 2 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 2 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 2 | [29 empty] | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 2 | [29 empty] | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 2 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 2 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 2 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 2 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 2 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 2 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 2 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 2 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 2 | [29 empty] | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 2 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 2 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 2 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 2 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 2 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 2 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 2 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 2 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 2 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 3 | [29 empty] | 0.66
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 3 | [29 empty] | 0.35
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 3 | [29 empty] | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 3 | [29 empty] | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 3 | [29 empty] | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 3 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 3 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 3 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 3 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 3 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 3 | [29 empty] | 0.33
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 3 | [29 empty] | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 3 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 3 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 3 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 3 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 3 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 3 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 3 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 3 | [11 empty] | 0.05 | 3 | [29 empty] | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 3 | [11 empty] | 0.1 | 3 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.15 | 3 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.2 | 3 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.25 | 3 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.3 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.35 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.4 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.45 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.5 | 3 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 1 | [11 empty] | 0.05 | 4 | [29 empty] | 0.75
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 1 | [11 empty] | 0.1 | 4 | [29 empty] | 0.39
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 4 | [29 empty] | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 4 | [29 empty] | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 4 | [29 empty] | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 4 | [29 empty] | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 4 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 4 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 4 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 4 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 4 | [29 empty] | 0.37
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 4 | [29 empty] | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 4 | [29 empty] | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 4 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 4 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 4 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 4 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 4 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 4 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 4 | [29 empty] | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 4 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 4 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 4 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 4 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 4 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 5 | [29 empty] | 0.84
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 5 | [29 empty] | 0.42
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 5 | [29 empty] | 0.26
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 5 | [29 empty] | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 5 | [29 empty] | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 5 | [29 empty] | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 5 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 5 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 5 | [29 empty] | 0.41
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 5 | [29 empty] | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 5 | [29 empty] | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 5 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 5 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 5 | [29 empty] | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 5 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 5 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 5 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 5 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 5 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 6 | [29 empty] | 0.93
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 6 | [29 empty] | 0.46
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 6 | [29 empty] | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 6 | [29 empty] | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 6 | [29 empty] | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 6 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 6 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 6 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 6 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 6 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 6 | [29 empty] | 0.45
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 6 | [29 empty] | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 6 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 6 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 6 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 6 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 6 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 6 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 6 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 6 | [29 empty] | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 6 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 6 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 6 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 6 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 6 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 7 | [29 empty] | 1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 7 | [29 empty] | 0.49
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 7 | [29 empty] | 0.3
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 7 | [29 empty] | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 7 | [29 empty] | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 7 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 7 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 7 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 7 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 7 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 7 | [29 empty] | 0.48
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 7 | [29 empty] | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 7 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 7 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 7 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 7 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 7 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 7 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 7 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 7 | [29 empty] | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 7 | [29 empty] | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 7 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 7 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 7 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 7 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.218 | 1 | [11 empty] | 0.05 | 8 | [29 empty] | 1.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.302 | 1 | [11 empty] | 0.1 | 8 | [29 empty] | 0.52
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.361 | 1 | [11 empty] | 0.15 | 8 | [29 empty] | 0.32
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.408 | 1 | [11 empty] | 0.2 | 8 | [29 empty] | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.447 | 1 | [11 empty] | 0.25 | 8 | [29 empty] | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.48 | 1 | [11 empty] | 0.3 | 8 | [29 empty] | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.509 | 1 | [11 empty] | 0.35 | 8 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.535 | 1 | [11 empty] | 0.4 | 8 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.557 | 1 | [11 empty] | 0.45 | 8 | [29 empty] | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.577 | 1 | [11 empty] | 0.5 | 8 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.362 | 2 | [11 empty] | 0.05 | 8 | [29 empty] | 0.51
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.45 | 2 | [11 empty] | 0.1 | 8 | [29 empty] | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.507 | 2 | [11 empty] | 0.15 | 8 | [29 empty] | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.55 | 2 | [11 empty] | 0.2 | 8 | [29 empty] | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.585 | 2 | [11 empty] | 0.25 | 8 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.613 | 2 | [11 empty] | 0.3 | 8 | [29 empty] | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.638 | 2 | [11 empty] | 0.35 | 8 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.659 | 2 | [11 empty] | 0.4 | 8 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.677 | 2 | [11 empty] | 0.45 | 8 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 2 | [11 empty] | 0.5 | 8 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.467 | 3 | [11 empty] | 0.05 | 8 | [29 empty] | 0.23
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.549 | 3 | [11 empty] | 0.1 | 8 | [29 empty] | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.601 | 3 | [11 empty] | 0.15 | 8 | [29 empty] | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.639 | 3 | [11 empty] | 0.2 | 8 | [29 empty] | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.669 | 3 | [11 empty] | 0.25 | 8 | [29 empty] | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.693 | 3 | [11 empty] | 0.3 | 8 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.714 | 3 | [11 empty] | 0.35 | 8 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.731 | 3 | [11 empty] | 0.4 | 8 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.746 | 3 | [11 empty] | 0.45 | 8 | [29 empty] | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [29 empty] | 0.76 | 3 | [11 empty] | 0.5 | 8 | [29 empty] | 0.01
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes |  | H (in) | W (in) | R (in) | S (in) | Q (cfm) | N/A | N/A | N/A |  |  | 2 | 1.5 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [5 empty] | 2 | 1.5 | [28 empty] | 1000 | [10 empty] | 0.24
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes |  | H (mm) | W (mm) | R (mm) | S (mm) | Q (m^3/hr) | N/A | N/A | N/A |  |  | 4.5 | 3.25 | [19 empty] | 2 | 1.5 | [28 empty] | 1500 | [10 empty] | 0.23
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 2 | 1.5 | [28 empty] | 2000 | [10 empty] | 0.22
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 2 | 1.5 | [28 empty] | 2500 | [10 empty] | 0.2
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 1000 | [10 empty] | 0.26
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 1500 | [10 empty] | 0.24
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 2000 | [10 empty] | 0.23
A7H1 | A-7 | Elbow | H | Rectangular | Mitered with Single thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 2500 | [10 empty] | 0.22
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes |  | H (in) | W (in) | R (in) | S (in) | Q (cfm) | N/A | N/A | N/A |  |  | 2 | 1.5 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [5 empty] | 2 | 1.5 | [28 empty] | 1000 | [10 empty] | 0.43
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes |  | H (mm) | W (mm) | R (mm) | S (mm) | Q (m^3/hr) | N/A | N/A | N/A |  |  | 2 | 2.25 | [19 empty] | 2 | 1.5 | [28 empty] | 1500 | [10 empty] | 0.42
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [11 empty] | 4.5 | 3.25 | [19 empty] | 2 | 1.5 | [28 empty] | 2000 | [10 empty] | 0.41
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 2 | 1.5 | [28 empty] | 2500 | [10 empty] | 0.4
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 2 | 2.25 | [28 empty] | 1000 | [10 empty] | 0.53
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 2 | 2.25 | [28 empty] | 1500 | [10 empty] | 0.53
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 2 | 2.25 | [28 empty] | 2000 | [10 empty] | 0.5
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 2 | 2.25 | [28 empty] | 2500 | [10 empty] | 0.49
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 1000 | [10 empty] | 0.27
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 1500 | [10 empty] | 0.25
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 2000 | [10 empty] | 0.24
A7H2 | A-7 | Elbow | H | Rectangular | Mitered with Double Thickness Turning Vanes | [32 empty] | 4.5 | 3.25 | [28 empty] | 2500 | [10 empty] | 0.23
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) |  | H (in) | W (in) | L (in) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [17 empty] | 0.25 | 0 | [26 empty] | 1.1 | 0
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) |  | H (mm) | W (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [35 empty] | 0.5 | 0.4 | [26 empty] | 1.07 | 0.62
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 0.75 | 0.6 | [26 empty] | 1.04 | 0.9
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 1 | 0.8 | [26 empty] | 1 | 1.6
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 1.5 | 1 | [26 empty] | 0.95 | 2.6
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 2 | 1.2 | [26 empty] | 0.9 | 3.6
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 3 | 1.4 | [26 empty] | 0.83 | 4
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 4 | 1.6 | [26 empty] | 0.78 | 4.2
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 6 | 1.8 | [26 empty] | 0.72 | 4.2
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [44 empty] | 8 | 2 | [26 empty] | 0.7 | 4.2
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 2.4 | [27 empty] | 3.7
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 2.8 | [27 empty] | 3.3
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 3.2 | [27 empty] | 3.2
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 4 | [27 empty] | 3.1
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 5 | [27 empty] | 2.9
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 6 | [27 empty] | 2.8
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 7 | [27 empty] | 2.7
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 9 | [27 empty] | 2.6
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 10 | [27 empty] | 2.5
A7I | A-7 | Elbow | I | Rectangular | Z-Shaped (W/H = 1) | [45 empty] | 12 | [27 empty] | 2.3
A7J | A-7 | Elbow | J | Rectangular | Different Planes |  | H (in) | W (in) | L (in) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [14 empty] | 0 |  | 1 | [29 empty] | 1.2
A7J | A-7 | Elbow | J | Rectangular | Different Planes |  | H (mm) | W (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [32 empty] | 0.4 |  | 1 | [29 empty] | 2.4
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 0.6 |  | 1 | [29 empty] | 2.9
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 0.8 |  | 1 | [29 empty] | 3.3
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 1 |  | 1 | [29 empty] | 3.4
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 1.2 |  | 1 | [29 empty] | 3.4
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 1.4 |  | 1 | [29 empty] | 3.4
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 1.6 |  | 1 | [29 empty] | 3.3
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 1.8 |  | 1 | [29 empty] | 3.2
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 2 |  | 1 | [29 empty] | 3.1
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 2.4 |  | 1 | [29 empty] | 3.2
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 2.8 |  | 1 | [29 empty] | 3.2
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 3.2 |  | 1 | [29 empty] | 3.2
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 4 |  | 1 | [29 empty] | 3
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 5 |  | 1 | [29 empty] | 2.9
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 6 |  | 1 | [29 empty] | 2.8
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 7 |  | 1 | [29 empty] | 2.7
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 9 |  | 1 | [29 empty] | 2.5
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 10 |  | 1 | [29 empty] | 2.4
A7J | A-7 | Elbow | J | Rectangular | Different Planes | [41 empty] | 12 |  | 1 | [29 empty] | 2.3
A7K | A-7 | Elbow | K | Round | 30° Offset |  | D (in) | L (in) | Q (cfm) | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | 0 | [35 empty] | 0
A7K | A-7 | Elbow | K | Round | 30° Offset |  | D (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | N/A | [28 empty] | 0.5 | [35 empty] | 0.15
A7K | A-7 | Elbow | K | Round | 30° Offset | [37 empty] | 1 | [35 empty] | 0.15
A7K | A-7 | Elbow | K | Round | 30° Offset | [37 empty] | 1.5 | [35 empty] | 0.16
A7K | A-7 | Elbow | K | Round | 30° Offset | [37 empty] | 2 | [35 empty] | 0.16
A7K | A-7 | Elbow | K | Round | 30° Offset | [37 empty] | 2.5 | [35 empty] | 0.16
A7K | A-7 | Elbow | K | Round | 30° Offset | [37 empty] | 3 | [35 empty] | 0.16
A7L | A-7 | Elbow | L | Rectangular | Wye or Tee Shape |  | W (in) | D (in) | D₁ (in) | L (in) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A
A7L | A-7 | Elbow | L | Rectangular | Wye or Tee Shape |  | W (mm) | D (mm) | D₁ (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion |  | D (in) | D₁ (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A | N/A |  |  | 16 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 2 | [18 empty] | 50000 |  | 16 |  |  | 0.14
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion |  | D (mm) | D₁ (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A | N/A |  |  | 20 | [37 empty] | 2 | [18 empty] | 50000 |  | 20 |  |  | 0.19
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 30 | [37 empty] | 2 | [18 empty] | 50000 |  | 30 |  |  | 0.32
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 45 | [37 empty] | 2 | [18 empty] | 50000 |  | 45 |  |  | 0.33
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 60 | [37 empty] | 2 | [18 empty] | 50000 |  | 60 |  |  | 0.33
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 90 | [37 empty] | 2 | [18 empty] | 50000 |  | 90 |  |  | 0.32
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 120 | [37 empty] | 2 | [18 empty] | 50000 |  | 120 |  |  | 0.31
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [11 empty] | 180 | [37 empty] | 2 | [18 empty] | 50000 |  | 180 |  |  | 0.3
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 16 |  |  | 0.23
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 20 |  |  | 0.3
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 30 |  |  | 0.46
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 45 |  |  | 0.61
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 60 |  |  | 0.68
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 90 |  |  | 0.64
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 120 |  |  | 0.63
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 50000 |  | 180 |  |  | 0.62
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 16 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 20 |  |  | 0.33
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 30 |  |  | 0.48
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 45 |  |  | 0.66
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 60 |  |  | 0.77
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 90 |  |  | 0.74
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 120 |  |  | 0.73
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 50000 |  | 180 |  |  | 0.72
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 16 |  |  | 0.29
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 20 |  |  | 0.38
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 30 |  |  | 0.59
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 45 |  |  | 0.76
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 60 |  |  | 0.8
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 90 |  |  | 0.83
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 120 |  |  | 0.84
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 50000 |  | 180 |  |  | 0.83
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 16 |  |  | 0.31
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 20 |  |  | 0.38
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 30 |  |  | 0.6
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 45 |  |  | 0.84
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 60 |  |  | 0.88
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 90 |  |  | 0.88
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 120 |  |  | 0.88
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 50000 |  | 180 |  |  | 0.88
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 16 |  |  | 0.07
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 20 |  |  | 0.12
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 30 |  |  | 0.23
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 45 |  |  | 0.28
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 60 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 90 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 120 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 200000 |  | 180 |  |  | 0.26
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 16 |  |  | 0.15
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 20 |  |  | 0.18
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 30 |  |  | 0.36
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 45 |  |  | 0.55
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 60 |  |  | 0.59
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 90 |  |  | 0.59
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 120 |  |  | 0.58
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 200000 |  | 180 |  |  | 0.57
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 16 |  |  | 0.19
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 20 |  |  | 0.28
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 30 |  |  | 0.44
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 45 |  |  | 0.9
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 60 |  |  | 0.7
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 90 |  |  | 0.71
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 120 |  |  | 0.71
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 200000 |  | 180 |  |  | 0.69
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 16 |  |  | 0.2
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 20 |  |  | 0.24
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 30 |  |  | 0.43
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 45 |  |  | 0.76
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 60 |  |  | 0.8
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 90 |  |  | 0.81
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 120 |  |  | 0.81
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 200000 |  | 180 |  |  | 0.81
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 16 |  |  | 0.21
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 20 |  |  | 0.28
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 30 |  |  | 0.52
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 45 |  |  | 0.76
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 60 |  |  | 0.87
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 90 |  |  | 0.87
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 120 |  |  | 0.87
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 200000 |  | 180 |  |  | 0.87
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 16 |  |  | 0.05
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 20 |  |  | 0.076
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 30 |  |  | 0.12
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 45 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 60 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 90 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 120 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 2 | [18 empty] | 600000 |  | 180 |  |  | 0.27
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 16 |  |  | 0.17
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 20 |  |  | 0.24
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 30 |  |  | 0.38
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 45 |  |  | 0.51
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 60 |  |  | 0.56
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 90 |  |  | 0.58
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 120 |  |  | 0.58
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 4 | [18 empty] | 600000 |  | 180 |  |  | 0.57
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 16 |  |  | 0.16
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 20 |  |  | 0.29
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 30 |  |  | 0.46
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 45 |  |  | 0.6
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 60 |  |  | 0.69
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 90 |  |  | 0.71
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 120 |  |  | 0.7
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 6 | [18 empty] | 600000 |  | 180 |  |  | 0.7
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 16 |  |  | 0.21
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 20 |  |  | 0.33
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 30 |  |  | 0.52
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 45 |  |  | 0.6
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 60 |  |  | 0.76
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 90 |  |  | 0.83
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 120 |  |  | 0.84
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 10 | [18 empty] | 600000 |  | 180 |  |  | 0.83
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 16 |  |  | 0.21
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 20 |  |  | 0.34
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 30 |  |  | 0.56
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 45 |  |  | 0.72
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 60 |  |  | 0.79
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 90 |  |  | 0.85
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 120 |  |  | 0.87
A8A | A-8 | Transition (Diverging Flow) | A | Round | Conical Expansion | [49 empty] | 16 | [18 empty] | 600000 |  | 180 |  |  | 0.89
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion |  | H (in) | W (in) | H₁ (in) | W₁ (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A |  |  |  |  | 16 |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 2 | [20 empty] | 16 |  |  | 0.18
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion |  | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A |  |  |  |  | 20 | [35 empty] | 2 | [20 empty] | 20 |  |  | 0.22
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 30 | [35 empty] | 2 | [20 empty] | 30 |  |  | 0.25
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 45 | [35 empty] | 2 | [20 empty] | 45 |  |  | 0.29
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 60 | [35 empty] | 2 | [20 empty] | 60 |  |  | 0.31
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 90 | [35 empty] | 2 | [20 empty] | 90 |  |  | 0.32
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 120 | [35 empty] | 2 | [20 empty] | 120 |  |  | 0.33
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [13 empty] | 180 | [35 empty] | 2 | [20 empty] | 180 |  |  | 0.3
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 16 |  |  | 0.36
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.43
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.5
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 45 |  |  | 0.56
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 60 |  |  | 0.61
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 90 |  |  | 0.63
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 120 |  |  | 0.63
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 4 | [20 empty] | 180 |  |  | 0.63
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 16 |  |  | 0.42
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 20 |  |  | 0.47
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 30 |  |  | 0.58
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 45 |  |  | 0.68
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 60 |  |  | 0.72
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 90 |  |  | 0.76
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 120 |  |  | 0.76
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 6 | [20 empty] | 180 |  |  | 0.75
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 16 |  |  | 0.42
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 20 |  |  | 0.49
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 30 |  |  | 0.59
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 45 |  |  | 0.7
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 60 |  |  | 0.8
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 90 |  |  | 0.87
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 120 |  |  | 0.85
A8B | A-8 | Transition (Diverging Flow) | B | Rectangular | Pyramidal Expansion | [49 empty] | 10 | [20 empty] | 180 |  |  | 0.86
A8C | A-8 | Transition (Diverging Flow) | C | Round | Round to Rectangular |  | H (in) | W (in) | D (in) | L (in) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A
A8C | A-8 | Transition (Diverging Flow) | C | Round | Round to Rectangular |  | H (mm) | W (mm) | D (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A
A8C | A-8 | Transition (Diverging Flow) | C | Round | Round to Rectangular
A8C | A-8 | Transition (Diverging Flow) | C | Round | Round to Rectangular
A8C | A-8 | Transition (Diverging Flow) | C | Round | Round to Rectangular | [70 empty] | θ=2*ATAN((1.13*SQRT(H*W)-D)/2*L)
A8D | A-8 | Transition (Diverging Flow) | D | Rectangular | Rectangular to Round |  | H (in) | W (in) | D (in) | L (in) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [43 empty] | angle=2*ATAN((D-1.13*SQRT(H*W))/2*L)
A8D | A-8 | Transition (Diverging Flow) | D | Rectangular | Rectangular to Round |  | H (mm) | W (mm) | D (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A
A8D | A-8 | Transition (Diverging Flow) | D | Rectangular | Rectangular to Round
A8D | A-8 | Transition (Diverging Flow) | D | Rectangular | Rectangular to Round
A8D | A-8 | Transition (Diverging Flow) | D | Rectangular | Rectangular to Round
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight |  | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A |  |  |  | 14 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 2 | [20 empty] | 14 |  |  | 0.09
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight |  | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 20 | [36 empty] | 2 | [20 empty] | 20 |  |  | 0.12
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [12 empty] | 30 | [36 empty] | 2 | [20 empty] | 30 |  |  | 0.2
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [12 empty] | 45 | [36 empty] | 2 | [20 empty] | 45 |  |  | 0.34
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [12 empty] | 60 | [36 empty] | 2 | [20 empty] | 60 |  |  | 0.37
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [12 empty] | 90 | [36 empty] | 2 | [20 empty] | 90 |  |  | 0.38
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [12 empty] | 180 | [36 empty] | 2 | [20 empty] | 180 |  |  | 0.35
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 14 |  |  | 0.16
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.25
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.42
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 45 |  |  | 0.6
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 60 |  |  | 0.68
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 90 |  |  | 0.7
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 4 | [20 empty] | 180 |  |  | 0.66
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 14 |  |  | 0.19
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 20 |  |  | 0.3
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 30 |  |  | 0.48
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 45 |  |  | 0.65
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 60 |  |  | 0.76
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 90 |  |  | 0.83
A8E | A-8 | Transition (Diverging Flow) | E | Rectangular | Rectangular Sides Strtaight | [49 empty] | 6 | [20 empty] | 180 |  |  | 0.8
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight |  | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A |  |  |  | 10 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.05
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight |  | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 15 | [36 empty] | 1.5 | [20 empty] | 15 |  |  | 0.06
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [12 empty] | 20 | [36 empty] | 1.5 | [20 empty] | 20 |  |  | 0.07
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [12 empty] | 25 | [36 empty] | 1.5 | [20 empty] | 25 |  |  | 0.08
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [12 empty] | 30 | [36 empty] | 1.5 | [20 empty] | 30 |  |  | 0.16
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [12 empty] | 35 | [36 empty] | 1.5 | [20 empty] | 35 |  |  | 0.24
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.07
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.09
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.1
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.13
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.24
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2 | [20 empty] | 35 |  |  | 0.34
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.09
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.11
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.13
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.16
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.29
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 2.5 | [20 empty] | 35 |  |  | 0.39
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.1
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.13
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.15
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.19
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.32
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3 | [20 empty] | 35 |  |  | 0.44
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.11
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.13
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.16
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.21
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.34
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 3.5 | [20 empty] | 35 |  |  | 0.48
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.11
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.14
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.16
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.23
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.35
A8F | A-8 | Transition (Diverging Flow) | F | Rectangular | Symmetric at Fan with Duct Sides Straight | [49 empty] | 4 | [20 empty] | 35 |  |  | 0.5
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level |  | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A |  |  |  | 10 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.08
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level |  | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 15 | [36 empty] | 1.5 | [20 empty] | 15 |  |  | 0.1
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [12 empty] | 20 | [36 empty] | 1.5 | [20 empty] | 20 |  |  | 0.12
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [12 empty] | 25 | [36 empty] | 1.5 | [20 empty] | 25 |  |  | 0.15
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [12 empty] | 30 | [36 empty] | 1.5 | [20 empty] | 30 |  |  | 0.18
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [12 empty] | 35 | [36 empty] | 1.5 | [20 empty] | 35 |  |  | 0.21
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.09
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.11
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.14
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.18
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.25
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2 | [20 empty] | 35 |  |  | 0.31
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.1
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.12
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.15
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.21
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.3
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 2.5 | [20 empty] | 35 |  |  | 0.38
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.1
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.13
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.16
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.23
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.33
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3 | [20 empty] | 35 |  |  | 0.41
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.11
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.14
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.17
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.25
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.35
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 3.5 | [20 empty] | 35 |  |  | 0.43
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.11
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.15
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.18
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.26
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.35
A8G | A-8 | Transition (Diverging Flow) | G | Rectangular | Asymmetric at Fan with Sides Straight, Top Level | [49 empty] | 4 | [20 empty] | 35 |  |  | 0.44
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down |  | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A |  |  |  | 10 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.11
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down |  | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 15 | [36 empty] | 1.5 | [20 empty] | 15 |  |  | 0.13
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [12 empty] | 20 | [36 empty] | 1.5 | [20 empty] | 20 |  |  | 0.19
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [12 empty] | 25 | [36 empty] | 1.5 | [20 empty] | 25 |  |  | 0.29
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [12 empty] | 30 | [36 empty] | 1.5 | [20 empty] | 30 |  |  | 0.36
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [12 empty] | 35 | [36 empty] | 1.5 | [20 empty] | 35 |  |  | 0.44
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.13
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.15
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.22
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.32
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.42
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2 | [20 empty] | 35 |  |  | 0.54
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.14
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.16
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.24
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.35
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.46
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 2.5 | [20 empty] | 35 |  |  | 0.61
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.14
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.17
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.26
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.37
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.49
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3 | [20 empty] | 35 |  |  | 0.64
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.14
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.18
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.28
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.39
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.51
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 3.5 | [20 empty] | 35 |  |  | 0.66
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.14
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.18
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.3
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.4
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.51
A8H | A-8 | Transition (Diverging Flow) | H | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Down | [49 empty] | 4 | [20 empty] | 35 |  |  | 0.66
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up |  | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A | N/A |  |  |  | 10 |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.05
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up |  | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A | N/A |  |  |  | 15 | [36 empty] | 1.5 | [20 empty] | 15 |  |  | 0.06
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [12 empty] | 20 | [36 empty] | 1.5 | [20 empty] | 20 |  |  | 0.07
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [12 empty] | 25 | [36 empty] | 1.5 | [20 empty] | 25 |  |  | 0.09
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [12 empty] | 30 | [36 empty] | 1.5 | [20 empty] | 30 |  |  | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [12 empty] | 35 | [36 empty] | 1.5 | [20 empty] | 35 |  |  | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.08
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.1
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.11
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.18
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2 | [20 empty] | 35 |  |  | 0.23
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.11
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.12
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.18
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.23
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 2.5 | [20 empty] | 35 |  |  | 0.28
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.2
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.26
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3 | [20 empty] | 35 |  |  | 0.33
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.16
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.21
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.28
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 3.5 | [20 empty] | 35 |  |  | 0.35
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.16
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.22
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.29
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [49 empty] | 4 | [20 empty] | 35 |  |  | 0.36
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct |  | H (in) | W (in) | H₁ (in) | W₁ (in) | θ (degrees) - select from list | Q (cfm) | N/A | N/A |  |  |  |  | 10 |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.1
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct |  | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | θ (degrees) - select from list | Q (m^3/hr) | N/A | N/A |  |  |  |  | 15 | [35 empty] | 1.5 | [20 empty] | 15 |  |  | 0.23
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [13 empty] | 20 | [35 empty] | 1.5 | [20 empty] | 20 |  |  | 0.31
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [13 empty] | 25 | [35 empty] | 1.5 | [20 empty] | 25 |  |  | 0.36
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [13 empty] | 30 | [35 empty] | 1.5 | [20 empty] | 30 |  |  | 0.42
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.18
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.33
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.43
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.49
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.53
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.21
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.38
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.48
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.55
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.59
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.23
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.4
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.53
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.58
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.64
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.24
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.42
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.56
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.62
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.67
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.25
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.44
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.58
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.64
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.69
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction |  | D (in) | D₁ (in) | θ (degrees) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 2 | [20 empty] | 10 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction |  | D (mm) | D₁ (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [40 empty] | 2 | [20 empty] | 40 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 2 | [20 empty] | 60 |  |  | 0.06
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 2 | [20 empty] | 90 |  |  | 0.12
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 2 | [20 empty] | 120 |  |  | 0.18
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 2 | [20 empty] | 150 |  |  | 0.24
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 2 | [20 empty] | 180 |  |  | 0.26
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 40 |  |  | 0.04
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 60 |  |  | 0.07
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 90 |  |  | 0.17
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 120 |  |  | 0.27
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 150 |  |  | 0.35
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 4 | [20 empty] | 180 |  |  | 0.41
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 10 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 40 |  |  | 0.04
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 60 |  |  | 0.07
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 90 |  |  | 0.18
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 120 |  |  | 0.28
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 150 |  |  | 0.36
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 6 | [20 empty] | 180 |  |  | 0.42
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 10 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 40 |  |  | 0.05
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 60 |  |  | 0.08
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 90 |  |  | 0.19
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 120 |  |  | 0.29
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 150 |  |  | 0.37
A9A1 | A-9 | Transition (Converging Flow) | A | Round | Conical Contraction | [49 empty] | 10 | [20 empty] | 180 |  |  | 0.43
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction |  | H (in) | W (in) | H₁ (in) | W₁ (in) | θ (degrees) | Q (cfm) | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 2 | [20 empty] | 10 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction |  | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | [40 empty] | 2 | [20 empty] | 40 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 2 | [20 empty] | 60 |  |  | 0.06
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 2 | [20 empty] | 90 |  |  | 0.12
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 2 | [20 empty] | 120 |  |  | 0.18
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 2 | [20 empty] | 150 |  |  | 0.24
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 2 | [20 empty] | 180 |  |  | 0.26
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 40 |  |  | 0.04
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 60 |  |  | 0.07
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 90 |  |  | 0.17
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 120 |  |  | 0.27
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 150 |  |  | 0.35
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 4 | [20 empty] | 180 |  |  | 0.41
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 10 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 40 |  |  | 0.04
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 60 |  |  | 0.07
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 90 |  |  | 0.18
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 120 |  |  | 0.28
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 150 |  |  | 0.36
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 6 | [20 empty] | 180 |  |  | 0.42
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 10 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 40 |  |  | 0.05
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 60 |  |  | 0.08
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 90 |  |  | 0.19
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 120 |  |  | 0.29
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 150 |  |  | 0.37
A9A2 | A-9 | Transition (Converging Flow) | A | Rectangular | Pyramidal Contraction | [49 empty] | 10 | [20 empty] | 180 |  |  | 0.43
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction |  | D (in) | D₁ (in) | L (in) | θ (degrees) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | 0.025 | [10 empty] | 0 | [21 empty] | 0 |  | 1 | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction |  | D (mm) | D₁ (mm) | L (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A | [28 empty] | 0.025 | [10 empty] | 0.2 | [21 empty] | 10 |  | 0.85 | 0.47
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [10 empty] | 0.4 | [21 empty] | 20 |  | 0.68 | 0.45
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [10 empty] | 0.8 | [21 empty] | 30 |  | 0.5 | 0.43
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [10 empty] | 0.8 | [21 empty] | 40 |  | 0.3 | 0.41
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [10 empty] | 0.9 | [21 empty] | 60 |  | 0.18 | 0.4
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [10 empty] | 1 | [21 empty] | 100 |  | 0 | 0.42
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 0 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 10 |  |  | 0.42
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 20 |  |  | 0.35
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 30 |  |  | 0.3
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 40 |  |  | 0.26
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 60 |  |  | 0.23
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 100 |  |  | 0.3
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 140 |  |  | 0.4
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.075 | [32 empty] | 180 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.39
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.32
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.25
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.22
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.18
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.27
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.38
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 0 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 10 |  |  | 0.37
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 20 |  |  | 0.27
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 30 |  |  | 0.2
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 40 |  |  | 0.16
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 60 |  |  | 0.15
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 100 |  |  | 0.25
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 140 |  |  | 0.37
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.15 | [32 empty] | 180 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.27
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.18
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.13
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.11
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.12
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.23
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.36
A9B1 | A-9 | Transition (Converging Flow) | B | Round | Stepped Conical Contraction | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction |  | H (in) | W (in) | H₁ (in) | W₁ (in) | L (in) | θ (degrees) | Q (cfm) | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.025 | [10 empty] | 0 | [21 empty] | 0 |  | 1 | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction |  | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | L (mm) | θ (degrees) | Q (m^3/hr) | N/A | [28 empty] | 0.025 | [10 empty] | 0.2 | [21 empty] | 10 |  | 0.85 | 0.47
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [10 empty] | 0.4 | [21 empty] | 20 |  | 0.68 | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [10 empty] | 0.8 | [21 empty] | 30 |  | 0.5 | 0.43
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [10 empty] | 0.8 | [21 empty] | 40 |  | 0.3 | 0.41
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [10 empty] | 0.9 | [21 empty] | 60 |  | 0.18 | 0.4
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [10 empty] | 1 | [21 empty] | 100 |  | 0 | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 0 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 10 |  |  | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 20 |  |  | 0.35
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 30 |  |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 40 |  |  | 0.26
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 60 |  |  | 0.23
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 100 |  |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 140 |  |  | 0.4
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.075 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.39
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.32
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.25
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.22
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.18
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.38
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 0 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 10 |  |  | 0.37
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 20 |  |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 30 |  |  | 0.2
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 40 |  |  | 0.16
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 60 |  |  | 0.15
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 100 |  |  | 0.25
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 140 |  |  | 0.37
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.15 | [32 empty] | 180 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.18
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.13
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.11
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.12
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.23
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.36
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round |  | D (in) | H₁ (in) | W₁ (in) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [47 empty] | 10000 | 1*10^4 |  |  |  | 0.27
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round |  | D (mm) | H₁ (mm) | W₁ (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [59 empty] | 20000 | 2*10^4 |  |  |  | 0.25
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 40000 | 4*10^4 |  |  |  | 0.2
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 60000 | 6*10^4 |  |  |  | 0.17
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 80000 | 8*10^4 |  |  |  | 0.14
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 100000 | 10*10^4 |  |  |  | 0.11
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 200000 | 20*10^4 |  |  |  | 0.04
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [68 empty] | 400000 | >=40*10^4 |  |  |  | 0
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | D_main (in) | D_branch (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.1 |  |  |  |  | 0.4 | [14 empty] | -0.56
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | D_main (mm) | D_branch (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [44 empty] | 0.1 |  |  |  |  | 0.5 | [14 empty] | -0.48
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 0.6 | [14 empty] | -0.38
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 0.7 | [14 empty] | -0.26
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 0.8 | [14 empty] | -0.21
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 0.9 | [14 empty] | 0.04
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 1 | [14 empty] | 0.22
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 1.5 | [14 empty] | 1.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 2 | [14 empty] | 3.1
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 2.5 | [14 empty] | 5.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.1 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.4 | [14 empty] | -0.44
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.5 | [14 empty] | -0.37
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.6 | [14 empty] | -0.27
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.7 | [14 empty] | -0.16
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.8 | [14 empty] | -0.02
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 0.9 | [14 empty] | 0.13
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 1 | [14 empty] | 0.31
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 1.5 | [14 empty] | 1.5
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 2 | [14 empty] | 3.2
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 2.5 | [14 empty] | 5.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.2 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.4 | [14 empty] | -0.35
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.5 | [14 empty] | -0.28
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.6 | [14 empty] | -0.19
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.7 | [14 empty] | -0.08
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.8 | [14 empty] | 0.05
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 0.9 | [14 empty] | 0.21
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 1 | [14 empty] | 0.38
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 1.5 | [14 empty] | 1.5
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 2 | [14 empty] | 3.2
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 2.5 | [14 empty] | 5.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.3 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.4 | [14 empty] | -0.28
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.5 | [14 empty] | -0.21
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.6 | [14 empty] | -0.12
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.7 | [14 empty] | -0.01
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.8 | [14 empty] | 0.12
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 0.9 | [14 empty] | 0.27
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 1 | [14 empty] | 0.44
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 1.5 | [14 empty] | 1.6
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 2 | [14 empty] | 3.2
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 2.5 | [14 empty] | 5.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.4 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.4 | [14 empty] | -0.15
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.5 | [14 empty] | -0.09
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.6 | [14 empty] | 0
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.7 | [14 empty] | 0.1
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.8 | [14 empty] | 0.23
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 0.9 | [14 empty] | 0.37
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 1 | [14 empty] | 0.53
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 1.5 | [14 empty] | 1.7
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 2 | [14 empty] | 3.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 2.5 | [14 empty] | 5.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.6 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.4 | [14 empty] | -0.04
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.5 | [14 empty] | 0.02
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.6 | [14 empty] | 0.1
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.7 | [14 empty] | 0.2
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.8 | [14 empty] | 0.32
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 0.9 | [14 empty] | 0.46
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 1 | [14 empty] | 0.62
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 1.5 | [14 empty] | 1.7
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 2 | [14 empty] | 3.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 2.5 | [14 empty] | 5.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 0.8 |  |  |  |  | 3 | [14 empty] | 8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.4 | [14 empty] | 0.05
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.5 | [14 empty] | 0.11
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.6 | [14 empty] | 0.18
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.7 | [14 empty] | 0.28
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.8 | [14 empty] | 0.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 0.9 | [14 empty] | 0.53
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 1 | [14 empty] | 0.69
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 1.5 | [14 empty] | 1.8
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 2 | [14 empty] | 3.3
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 2.5 | [14 empty] | 5.4
A10A1 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | branch | [52 empty] | 1 |  |  |  |  | 3 | [14 empty] | 8
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.1 | [5 empty] | 0.1 | [13 empty] | -8.6
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.2 | [13 empty] | -6.7
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.3 | [13 empty] | -5
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.4 | [13 empty] | -3.5
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.5 | [13 empty] | -2.3
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.6 | [13 empty] | -1.3
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.7 | [13 empty] | -0.63
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.8 | [13 empty] | -0.18
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 0.9 | [13 empty] | 0.03
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.1 | [5 empty] | 1 | [13 empty] | -0.01
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.1 | [13 empty] | -4.1
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.2 | [13 empty] | -3.1
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.3 | [13 empty] | -2.2
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.4 | [13 empty] | -1.5
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.5 | [13 empty] | -0.95
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.6 | [13 empty] | -0.5
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.7 | [13 empty] | -0.18
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.8 | [13 empty] | 0.01
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 0.9 | [13 empty] | 0.07
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.2 | [5 empty] | 1 | [13 empty] | 0
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.1 | [13 empty] | -2.5
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.2 | [13 empty] | -1.9
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.3 | [13 empty] | -1.3
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.4 | [13 empty] | -0.88
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.5 | [13 empty] | -0.51
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.6 | [13 empty] | -0.22
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.7 | [13 empty] | -0.03
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.8 | [13 empty] | 0.07
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 0.9 | [13 empty] | 0.08
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.3 | [5 empty] | 1 | [13 empty] | 0
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.1 | [13 empty] | -1.7
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.2 | [13 empty] | -1.3
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.3 | [13 empty] | -0.88
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.4 | [13 empty] | -0.55
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.5 | [13 empty] | -0.28
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.6 | [13 empty] | -0.09
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.7 | [13 empty] | 0.04
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.8 | [13 empty] | 0.1
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 0.9 | [13 empty] | 0.09
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.4 | [5 empty] | 1 | [13 empty] | 0.1
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.1 | [13 empty] | -0.97
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.2 | [13 empty] | -0.67
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.3 | [13 empty] | -0.42
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.4 | [13 empty] | -0.21
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.5 | [13 empty] | -0.06
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.6 | [13 empty] | 0.05
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.7 | [13 empty] | 0.12
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.8 | [13 empty] | 0.13
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 0.9 | [13 empty] | 0.1
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.6 | [5 empty] | 1 | [13 empty] | 0.02
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.1 | [13 empty] | -0.58
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.2 | [13 empty] | -0.36
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.3 | [13 empty] | -0.19
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.4 | [13 empty] | -0.05
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.5 | [13 empty] | 0.06
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.6 | [13 empty] | 0.12
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.7 | [13 empty] | 0.16
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.8 | [13 empty] | 0.15
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 0.9 | [13 empty] | 0.11
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 0.8 | [5 empty] | 1 | [13 empty] | 0.04
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.1 | [13 empty] | -0.34
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.2 | [13 empty] | -0.18
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.3 | [13 empty] | -0.05
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.4 | [13 empty] | 0.05
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.5 | [13 empty] | 0.13
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.6 | [13 empty] | 0.17
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.7 | [13 empty] | 0.18
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.8 | [13 empty] | 0.17
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 0.9 | [13 empty] | 0.13
A10A2 | A-10 | Converging Junctions (Tees, Wyes) | A | Round | Round Converging Wye | main | [52 empty] | 1 | [5 empty] | 1 | [13 empty] | 0.05
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | D_main (in) | D_branch (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.1 | [10 empty] | 0.1 | [8 empty] | 0.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | D_main (mm) | D_branch (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [44 empty] | 0.1 | [10 empty] | 0.2 | [8 empty] | 3.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.3 | [8 empty] | 9.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.4 | [8 empty] | 16
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.5 | [8 empty] | 26
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.6 | [8 empty] | 37
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.7 | [8 empty] | 43
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.8 | [8 empty] | 65
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | 82
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.1 | [10 empty] | 1 | [8 empty] | 101
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.1 | [8 empty] | -0.37
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.2 | [8 empty] | 0.72
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.3 | [8 empty] | 2.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.4 | [8 empty] | 4.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.5 | [8 empty] | 6.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.6 | [8 empty] | 9.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.7 | [8 empty] | 13
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.8 | [8 empty] | 17
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.9 | [8 empty] | 21
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.2 | [10 empty] | 1 | [8 empty] | 26
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.1 | [8 empty] | -0.51
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.2 | [8 empty] | 0.17
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.3 | [8 empty] | 1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.4 | [8 empty] | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.5 | [8 empty] | 3.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.6 | [8 empty] | 4.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.7 | [8 empty] | 6.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.8 | [8 empty] | 7.9
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.9 | [8 empty] | 9.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.3 | [10 empty] | 1 | [8 empty] | 12
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.1 | [8 empty] | -0.46
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.2 | [8 empty] | -0.02
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.3 | [8 empty] | 0.44
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.4 | [8 empty] | 0.94
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.5 | [8 empty] | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.6 | [8 empty] | 1.6
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.7 | [8 empty] | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.8 | [8 empty] | 2.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.9 | [8 empty] | 3.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.4 | [10 empty] | 1 | [8 empty] | 4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.1 | [8 empty] | -0.5
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.2 | [8 empty] | -0.14
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.3 | [8 empty] | 0.21
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.4 | [8 empty] | 0.54
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.5 | [8 empty] | 0.66
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.6 | [8 empty] | 0.92
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.7 | [8 empty] | 1.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.8 | [8 empty] | 1.5
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.9 | [8 empty] | 1.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.6 | [10 empty] | 1 | [8 empty] | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.1 | [8 empty] | -0.51
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.2 | [8 empty] | -0.18
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.3 | [8 empty] | 0.11
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.4 | [8 empty] | 0.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.5 | [8 empty] | 0.49
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.6 | [8 empty] | 0.69
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.7 | [8 empty] | 0.88
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.8 | [8 empty] | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.9 | [8 empty] | 1.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 0.8 | [10 empty] | 1 | [8 empty] | 1.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.1 | [8 empty] | -0.52
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.2 | [8 empty] | -0.24
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.3 | [8 empty] | -0.08
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.4 | [8 empty] | 0.32
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.5 | [8 empty] | 0.42
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.6 | [8 empty] | 0.57
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.7 | [8 empty] | 0.72
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.8 | [8 empty] | 0.86
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 0.9 | [8 empty] | 0.99
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [52 empty] | 1 | [10 empty] | 1 | [8 empty] | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [43 empty] | 0.1 | [8 empty] | 0.16
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.2 | [8 empty] | 0.27
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.3 | [8 empty] | 0.38
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.4 | [8 empty] | 0.46
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.5 | [8 empty] | 0.53
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.6 | [8 empty] | 0.57
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.7 | [8 empty] | 0.59
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.8 | [8 empty] | 0.6
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 0.9 | [8 empty] | 0.59
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [63 empty] | 1 | [8 empty] | 0.55
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | H_s (in) | W_s (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [30 empty] | 0 | [6 empty] | 0.1 | [8 empty] | -0.63
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | H_s (mm) | W_s (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [48 empty] | 0 | [6 empty] | 0.2 | [8 empty] | -0.55
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.3 | [8 empty] | 0.13
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.4 | [8 empty] | 0.23
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.5 | [8 empty] | 0.78
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.6 | [8 empty] | 1.3
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.7 | [8 empty] | 1.93
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.8 | [8 empty] | 3.1
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.9 | [8 empty] | 4.88
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 1 | [8 empty] | 5.6
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.1 | [8 empty] | -0.49
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.2 | [8 empty] | -0.21
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.3 | [8 empty] | 0.23
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.4 | [8 empty] | 0.6
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.5 | [8 empty] | 1.27
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.6 | [8 empty] | 2.06
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.7 | [8 empty] | 2.75
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.8 | [8 empty] | 3.7
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.9 | [8 empty] | 4.93
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 1 | [8 empty] | 5.95
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | H_s (in) | W_s (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [30 empty] | 0 | [6 empty] | 0.1 | [8 empty] | -0.75
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | H_s (mm) | W_s (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [48 empty] | 0 | [6 empty] | 0.2 | [8 empty] | -0.53
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.3 | [8 empty] | -0.03
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.4 | [8 empty] | 0.33
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.5 | [8 empty] | 1.03
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.6 | [8 empty] | 1.1
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.7 | [8 empty] | 2.15
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.8 | [8 empty] | 2.93
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 0.9 | [8 empty] | 4.18
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 0 | [6 empty] | 1 | [8 empty] | 4.78
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.1 | [8 empty] | -0.69
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.2 | [8 empty] | -0.21
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.3 | [8 empty] | 0.23
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.4 | [8 empty] | 0.67
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.5 | [8 empty] | 1.17
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.6 | [8 empty] | 1.66
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.7 | [8 empty] | 2.67
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.8 | [8 empty] | 3.36
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 0.9 | [8 empty] | 3.93
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [56 empty] | 1200 | [6 empty] | 1 | [8 empty] | 5.13
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | D_s (in) | D_c (in) | D_b (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.2 | 0.3 | [10 empty] | 0.2 | [7 empty] | -2.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | D_s (mm) | D_c (mm) | D_b (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | [44 empty] | 0.2 | 0.3 | [10 empty] | 0.4 | [7 empty] | -0.01
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 0.6 | [7 empty] | 2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 0.8 | [7 empty] | 3.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 1 | [7 empty] | 5.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.2 | [7 empty] | 6.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.4 | [7 empty] | 7.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.6 | [7 empty] | 8.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.8 | [7 empty] | 9.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.3 | [10 empty] | 2 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.2 | [7 empty] | -2.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.4 | [7 empty] | -1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.6 | [7 empty] | 0.12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.8 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 1 | [7 empty] | 1.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.2 | [7 empty] | 2.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.4 | [7 empty] | 3.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.6 | [7 empty] | 3.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.8 | [7 empty] | 4.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.3 | [10 empty] | 2 | [7 empty] | 4.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.2 | [7 empty] | -1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.4 | [7 empty] | 0.93
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.6 | [7 empty] | 2.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.8 | [7 empty] | 4.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 1 | [7 empty] | 5.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.2 | [7 empty] | 7.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.4 | [7 empty] | 8.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.6 | [7 empty] | 9.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.8 | [7 empty] | 10
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.4 | [10 empty] | 2 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.2 | [7 empty] | -1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.4 | [7 empty] | -0.27
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.6 | [7 empty] | 0.81
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.8 | [7 empty] | 1.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 1 | [7 empty] | 2.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.2 | [7 empty] | 3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.4 | [7 empty] | 3.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.6 | [7 empty] | 4.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.8 | [7 empty] | 4.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.4 | [10 empty] | 2 | [7 empty] | 4.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.2 | [7 empty] | -1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.4 | [7 empty] | -0.72
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.6 | [7 empty] | 0.07
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.8 | [7 empty] | 0.66
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 1 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.2 | [7 empty] | 1.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.4 | [7 empty] | 1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.6 | [7 empty] | 2.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.8 | [7 empty] | 2.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.4 | [10 empty] | 2 | [7 empty] | 2.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.2 | [7 empty] | -0.46
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.4 | [7 empty] | 1.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.6 | [7 empty] | 3.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.8 | [7 empty] | 4.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 1 | [7 empty] | 6.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.2 | [7 empty] | 7.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.4 | [7 empty] | 8.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.6 | [7 empty] | 9.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.8 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.5 | [10 empty] | 2 | [7 empty] | 12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.2 | [7 empty] | -0.94
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.4 | [7 empty] | 0.25
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.6 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.8 | [7 empty] | 2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 1 | [7 empty] | 2.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.2 | [7 empty] | 3.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.4 | [7 empty] | 3.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.6 | [7 empty] | 4.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.8 | [7 empty] | 4.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.5 | [10 empty] | 2 | [7 empty] | 5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.2 | [7 empty] | -1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.4 | [7 empty] | -0.24
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.6 | [7 empty] | 0.42
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.8 | [7 empty] | 0.92
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 1 | [7 empty] | 1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.2 | [7 empty] | 1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.4 | [7 empty] | 1.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.6 | [7 empty] | 2.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.8 | [7 empty] | 2.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.5 | [10 empty] | 2 | [7 empty] | 2.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.2 | [7 empty] | -1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.4 | [7 empty] | -0.38
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.6 | [7 empty] | 0.18
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.8 | [7 empty] | 0.58
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 1 | [7 empty] | 0.88
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.2 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.4 | [7 empty] | 1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.6 | [7 empty] | 1.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.8 | [7 empty] | 1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.5 | [10 empty] | 2 | [7 empty] | 1.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.2 | [7 empty] | -0.55
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.4 | [7 empty] | 1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.6 | [7 empty] | 3.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.8 | [7 empty] | 4.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 1 | [7 empty] | 6.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.2 | [7 empty] | 7.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.4 | [7 empty] | 8.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.6 | [7 empty] | 9.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.8 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.6 | [10 empty] | 2 | [7 empty] | 12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.2 | [7 empty] | -1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.6 | [7 empty] | 0.88
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.8 | [7 empty] | 1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 1 | [7 empty] | 2.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.2 | [7 empty] | 2.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.4 | [7 empty] | 3.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.6 | [7 empty] | 3.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.8 | [7 empty] | 4.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.6 | [10 empty] | 2 | [7 empty] | 4.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.2 | [7 empty] | -1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.4 | [7 empty] | -0.48
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.6 | [7 empty] | 0.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.8 | [7 empty] | 0.54
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 1 | [7 empty] | 0.89
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.2 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.4 | [7 empty] | 1.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.6 | [7 empty] | 1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.8 | [7 empty] | 1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.6 | [10 empty] | 2 | [7 empty] | 2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.2 | [7 empty] | -1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.4 | [7 empty] | -0.62
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.6 | [7 empty] | -0.14
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.8 | [7 empty] | 0.21
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 1 | [7 empty] | 0.47
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.2 | [7 empty] | 0.68
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.4 | [7 empty] | 0.85
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.6 | [7 empty] | 0.99
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.8 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.6 | [10 empty] | 2 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.2 | [7 empty] | -1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.4 | [7 empty] | -0.69
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.6 | [7 empty] | -0.26
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.8 | [7 empty] | 0.04
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 1 | [7 empty] | 0.26
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.2 | [7 empty] | 0.42
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.4 | [7 empty] | 0.57
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.6 | [7 empty] | 0.66
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.8 | [7 empty] | 0.75
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.6 | [10 empty] | 2 | [7 empty] | 0.82
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.06
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.4 | [7 empty] | 1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.6 | [7 empty] | 3.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.8 | [7 empty] | 5.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 1 | [7 empty] | 6.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.2 | [7 empty] | 7.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.4 | [7 empty] | 8.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.6 | [7 empty] | 10
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.8 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 0.8 | [10 empty] | 2 | [7 empty] | 12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.52
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.35
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.6 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.8 | [7 empty] | 1.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 1 | [7 empty] | 2.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.2 | [7 empty] | 2.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.4 | [7 empty] | 3.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.6 | [7 empty] | 3.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.8 | [7 empty] | 3.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 0.8 | [10 empty] | 2 | [7 empty] | 4.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.67
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.05
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.43
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 1 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.2 | [7 empty] | 1.4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.4 | [7 empty] | 1.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.6 | [7 empty] | 1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.8 | [7 empty] | 1.9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 0.8 | [10 empty] | 2 | [7 empty] | 2.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.73
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.19
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.18
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.46
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 1 | [7 empty] | 0.68
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.2 | [7 empty] | 0.85
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.4 | [7 empty] | 0.99
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.6 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.8 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 0.8 | [10 empty] | 2 | [7 empty] | 1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.75
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.27
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.05
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.28
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 1 | [7 empty] | 0.45
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.2 | [7 empty] | 0.58
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.4 | [7 empty] | 0.68
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.6 | [7 empty] | 0.76
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.8 | [7 empty] | 0.83
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 0.8 | [10 empty] | 2 | [7 empty] | 0.88
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.77
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.31
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.6 | [7 empty] | -0.02
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.18
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 1 | [7 empty] | 0.32
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.2 | [7 empty] | 0.43
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.4 | [7 empty] | 0.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.6 | [7 empty] | 0.56
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.8 | [7 empty] | 0.61
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.7 | 0.8 | [10 empty] | 2 | [7 empty] | 0.65
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.78
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.34
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.6 | [7 empty] | -0.07
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 1 | [7 empty] | 0.24
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.2 | [7 empty] | 0.33
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.4 | [7 empty] | 0.39
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.6 | [7 empty] | 0.44
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.8 | [7 empty] | 0.47
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 0.8 | [10 empty] | 2 | [7 empty] | 0.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 0.4 | [7 empty] | 2.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 0.6 | [7 empty] | 3.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 0.8 | [7 empty] | 5.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 1 | [7 empty] | 6.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 1.2 | [7 empty] | 7.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 1.4 | [7 empty] | 9
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 1.6 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 1.8 | [7 empty] | 11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.2 | 1 | [10 empty] | 2 | [7 empty] | 12
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 0.4 | [7 empty] | 0.54
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 0.6 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 0.8 | [7 empty] | 1.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 1 | [7 empty] | 2.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 1.2 | [7 empty] | 2.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 1.4 | [7 empty] | 3.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 1.6 | [7 empty] | 3.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 1.8 | [7 empty] | 3.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.3 | 1 | [10 empty] | 2 | [7 empty] | 4
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 0.4 | [7 empty] | 0.21
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 0.6 | [7 empty] | 0.62
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 0.8 | [7 empty] | 0.96
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 1 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 1.2 | [7 empty] | 1.5
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 1.4 | [7 empty] | 1.7
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 1.6 | [7 empty] | 2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 1.8 | [7 empty] | 2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.4 | 1 | [10 empty] | 2 | [7 empty] | 2.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 0.4 | [7 empty] | 0.05
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 0.6 | [7 empty] | 0.37
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 0.8 | [7 empty] | 0.6
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 1 | [7 empty] | 0.79
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 1.2 | [7 empty] | 0.93
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 1.4 | [7 empty] | 1.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 1.6 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 1.8 | [7 empty] | 1.2
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.5 | 1 | [10 empty] | 2 | [7 empty] | 1.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 0.4 | [7 empty] | -0.02
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 0.6 | [7 empty] | 0.23
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 0.8 | [7 empty] | 0.42
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 1 | [7 empty] | 0.55
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 1.2 | [7 empty] | 0.66
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 1.4 | [7 empty] | 0.73
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 1.6 | [7 empty] | 0.8
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 1.8 | [7 empty] | 0.85
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.6 | 1 | [10 empty] | 2 | [7 empty] | 0.89
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 0.4 | [7 empty] | -0.1
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 0.6 | [7 empty] | 0.11
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 0.8 | [7 empty] | 0.24
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 1 | [7 empty] | 0.33
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 1.2 | [7 empty] | 0.39
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 1.4 | [7 empty] | 0.43
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 1.6 | [7 empty] | 0.46
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 1.8 | [7 empty] | 0.47
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 0.8 | 1 | [10 empty] | 2 | [7 empty] | 0.48
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 0.4 | [7 empty] | -0.14
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 0.6 | [7 empty] | 0.05
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 0.8 | [7 empty] | 0.16
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 1 | [7 empty] | 0.23
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 1.2 | [7 empty] | 0.27
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 1.4 | [7 empty] | 0.29
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 1.6 | [7 empty] | 0.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 1.8 | [7 empty] | 0.3
A10E | A-10 | Converging Junctions (Tees, Wyes) | E | Round | Converging Wye, Conical | branch | [52 empty] | 1 | 1 | [10 empty] | 2 | [7 empty] | 0.29
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | H_s (in) | W_s (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [30 empty] | 0 | [6 empty] | 0.1 | [8 empty] | -0.83
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | H_s (mm) | W_s (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [48 empty] | 0 | [6 empty] | 0.2 | [8 empty] | -0.68
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.3 | [8 empty] | -0.3
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.4 | [8 empty] | 0.28
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.5 | [8 empty] | 0.55
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.6 | [8 empty] | 1.03
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.7 | [8 empty] | 1.5
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.8 | [8 empty] | 1.93
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 0.9 | [8 empty] | 2.5
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 0 | [6 empty] | 1 | [8 empty] | 3.03
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.1 | [8 empty] | -0.72
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.2 | [8 empty] | -0.52
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.3 | [8 empty] | -0.23
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.4 | [8 empty] | 0.34
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.5 | [8 empty] | 0.76
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.6 | [8 empty] | 1.14
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.7 | [8 empty] | 1.83
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.8 | [8 empty] | 2.01
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 0.9 | [8 empty] | 2.9
A10F | A-10 | Converging Junctions (Tees, Wyes) | F | Rectangular | Converging Tee, 45 Entry Branch to Rectangular Main | branch | [56 empty] | 1200 | [6 empty] | 1 | [8 empty] | 3.63
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [16 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.2 | 0.3 | [10 empty] | 0.2 | [7 empty] | 5.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 0.4 | [7 empty] | -0.01
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 0.6 | [7 empty] | 2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 0.8 | [7 empty] | 1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 1 | [7 empty] | 0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.2 | [7 empty] | -0.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.4 | [7 empty] | -0.61
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.6 | [7 empty] | -0.93
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 1.8 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.3 | [10 empty] | 2 | [7 empty] | -1.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.2 | [7 empty] | 5.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.4 | [7 empty] | 3.7
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.6 | [7 empty] | 2.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 0.8 | [7 empty] | 1.6
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 1 | [7 empty] | 1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.2 | [7 empty] | 0.53
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.4 | [7 empty] | 0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.6 | [7 empty] | -0.14
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 1.8 | [7 empty] | -0.38
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.3 | [10 empty] | 2 | [7 empty] | -0.58
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.2 | [7 empty] | 1.9
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.4 | [7 empty] | 1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.6 | [7 empty] | 0.46
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 0.8 | [7 empty] | -0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 1 | [7 empty] | -0.49
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.2 | [7 empty] | -0.83
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.4 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.6 | [7 empty] | -1.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 1.8 | [7 empty] | -1.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.4 | [10 empty] | 2 | [7 empty] | -1.7
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.2 | [7 empty] | 2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.4 | [7 empty] | 1.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.6 | [7 empty] | 0.81
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 0.8 | [7 empty] | 0.42
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 1 | [7 empty] | 0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.2 | [7 empty] | -0.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.4 | [7 empty] | -0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.6 | [7 empty] | -0.62
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 1.8 | [7 empty] | -0.78
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.4 | [10 empty] | 2 | [7 empty] | -0.92
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.2 | [7 empty] | 2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.4 | [7 empty] | 1.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.6 | [7 empty] | 1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 0.8 | [7 empty] | 0.68
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 1 | [7 empty] | 0.39
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.2 | [7 empty] | 0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.4 | [7 empty] | -0.04
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.6 | [7 empty] | -0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 1.8 | [7 empty] | -0.35
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.4 | [10 empty] | 2 | [7 empty] | -0.47
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.2 | [7 empty] | 0.77
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.4 | [7 empty] | 0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.6 | [7 empty] | -0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 0.8 | [7 empty] | -0.48
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 1 | [7 empty] | -0.81
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.2 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.4 | [7 empty] | 1.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.6 | [7 empty] | -1.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 1.8 | [7 empty] | -1.7
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.5 | [10 empty] | 2 | [7 empty] | -1.8
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.2 | [7 empty] | 0.85
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.4 | [7 empty] | 0.56
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.6 | [7 empty] | 0.25
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 0.8 | [7 empty] | -0.03
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 1 | [7 empty] | -0.27
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.2 | [7 empty] | -0.48
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.4 | [7 empty] | -0.67
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.6 | [7 empty] | -0.82
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 1.8 | [7 empty] | -0.96
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.5 | [10 empty] | 2 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.2 | [7 empty] | 0.88
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.4 | [7 empty] | 0.66
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.6 | [7 empty] | 0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 0.8 | [7 empty] | 0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 1 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.2 | [7 empty] | -0.15
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.4 | [7 empty] | -0.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.6 | [7 empty] | -0.42
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 1.8 | [7 empty] | -0.54
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.5 | [10 empty] | 2 | [7 empty] | -0.64
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.2 | [7 empty] | 0.91
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.4 | [7 empty] | 0.73
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.6 | [7 empty] | 0.54
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 0.8 | [7 empty] | 0.36
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 1 | [7 empty] | 0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.2 | [7 empty] | 0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.4 | [7 empty] | -0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.6 | [7 empty] | -0.17
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 1.8 | [7 empty] | -0.26
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.5 | [10 empty] | 2 | [7 empty] | -0.35
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.2 | [7 empty] | 0.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.6 | [7 empty] | -0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 0.8 | [7 empty] | -0.67
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 1 | [7 empty] | -0.96
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.2 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.4 | [7 empty] | -1.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.6 | [7 empty] | -1.6
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 1.8 | [7 empty] | -1.8
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.6 | [10 empty] | 2 | [7 empty] | -1.9
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.2 | [7 empty] | 0.37
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.6 | [7 empty] | -0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 0.8 | [7 empty] | -0.24
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 1 | [7 empty] | -0.44
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.2 | [7 empty] | -0.63
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.4 | [7 empty] | -0.79
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.6 | [7 empty] | -0.93
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 1.8 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.6 | [10 empty] | 2 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.2 | [7 empty] | 0.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0.31
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.6 | [7 empty] | 0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 0.8 | [7 empty] | -0.01
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 1 | [7 empty] | -0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.2 | [7 empty] | -0.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.4 | [7 empty] | -0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.6 | [7 empty] | -0.54
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 1.8 | [7 empty] | -0.64
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.6 | [10 empty] | 2 | [7 empty] | -0.73
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.2 | [7 empty] | 0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0.37
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.6 | [7 empty] | 0.26
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 0.8 | [7 empty] | 0.14
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 1 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.2 | [7 empty] | -0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.4 | [7 empty] | -0.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.6 | [7 empty] | -0.29
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 1.8 | [7 empty] | -0.37
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.6 | [10 empty] | 2 | [7 empty] | -0.45
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.2 | [7 empty] | 0.44
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.4 | [7 empty] | 0.41
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.6 | [7 empty] | 0.33
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 0.8 | [7 empty] | 0.24
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 1 | [7 empty] | 0.14
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.2 | [7 empty] | 0.05
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.4 | [7 empty] | -0.03
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.6 | [7 empty] | -0.11
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 1.8 | [7 empty] | -0.18
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.6 | [10 empty] | 2 | [7 empty] | -0.25
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.2 | [7 empty] | -0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.27
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.6 | [7 empty] | -0.57
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 0.8 | [7 empty] | -0.86
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 1 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.2 | [7 empty] | -1.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.4 | [7 empty] | -1.6
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.6 | [7 empty] | -1.7
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 1.8 | [7 empty] | -1.9
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 0.8 | [10 empty] | 2 | [7 empty] | -2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.4 | [7 empty] | -0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.6 | [7 empty] | -0.25
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 0.8 | [7 empty] | -0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 1 | [7 empty] | -0.62
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.2 | [7 empty] | -0.78
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.4 | [7 empty] | -0.93
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.6 | [7 empty] | -1.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 1.8 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 0.8 | [10 empty] | 2 | [7 empty] | -1.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.04
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.6 | [7 empty] | -0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 0.8 | [7 empty] | -0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 1 | [7 empty] | -0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.2 | [7 empty] | -0.46
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.4 | [7 empty] | -0.57
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.6 | [7 empty] | -0.67
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 1.8 | [7 empty] | -0.77
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 0.8 | [10 empty] | 2 | [7 empty] | -0.85
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 0.8 | [7 empty] | -0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 1 | [7 empty] | -0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.2 | [7 empty] | -0.25
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.4 | [7 empty] | -0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.6 | [7 empty] | -0.42
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 1.8 | [7 empty] | -0.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 0.8 | [10 empty] | 2 | [7 empty] | -0.57
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.12
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.03
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 1 | [7 empty] | -0.04
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.2 | [7 empty] | -0.11
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.4 | [7 empty] | -0.18
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.6 | [7 empty] | -0.25
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 1.8 | [7 empty] | -0.31
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 0.8 | [10 empty] | 2 | [7 empty] | -0.37
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.15
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.14
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 1 | [7 empty] | 0.05
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.2 | [7 empty] | -0.01
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.4 | [7 empty] | -0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.6 | [7 empty] | -0.12
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 1.8 | [7 empty] | -0.17
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.7 | 0.8 | [10 empty] | 2 | [7 empty] | -0.22
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.2 | [7 empty] | 0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.4 | [7 empty] | 0.17
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.6 | [7 empty] | 0.18
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 0.8 | [7 empty] | 0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 1 | [7 empty] | 0.11
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.2 | [7 empty] | 0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.4 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.6 | [7 empty] | -0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 1.8 | [7 empty] | -0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 0.8 | [10 empty] | 2 | [7 empty] | -0.11
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 0.4 | [7 empty] | -0.39
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 0.6 | [7 empty] | -0.67
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 0.8 | [7 empty] | -0.96
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 1 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 1.2 | [7 empty] | -1.5
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 1.4 | [7 empty] | -1.6
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 1.6 | [7 empty] | -1.8
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 1.8 | [7 empty] | -2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.2 | 1 | [10 empty] | 2 | [7 empty] | -2.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 0.4 | [7 empty] | -0.19
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 0.6 | [7 empty] | -0.35
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 0.8 | [7 empty] | -0.54
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 1 | [7 empty] | -0.71
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 1.2 | [7 empty] | -0.87
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 1.4 | [7 empty] | -1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 1.6 | [7 empty] | -1.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 1.8 | [7 empty] | -1.3
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.3 | 1 | [10 empty] | 2 | [7 empty] | -1.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 0.4 | [7 empty] | -0.1
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 0.6 | [7 empty] | -0.19
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 0.8 | [7 empty] | -0.31
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 1 | [7 empty] | -0.43
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 1.2 | [7 empty] | -0.55
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 1.4 | [7 empty] | -0.66
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 1.6 | [7 empty] | -0.77
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 1.8 | [7 empty] | -0.86
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.4 | 1 | [10 empty] | 2 | [7 empty] | -0.94
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 0.4 | [7 empty] | -0.04
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 0.6 | [7 empty] | -0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 0.8 | [7 empty] | -0.17
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 1 | [7 empty] | -0.26
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 1.2 | [7 empty] | -0.35
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 1.4 | [7 empty] | -0.44
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 1.6 | [7 empty] | -0.52
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 1.8 | [7 empty] | -0.59
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.5 | 1 | [10 empty] | 2 | [7 empty] | -0.66
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 0.4 | [7 empty] | 0
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 0.6 | [7 empty] | -0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 0.8 | [7 empty] | -0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 1 | [7 empty] | -0.14
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 1.2 | [7 empty] | -0.21
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 1.4 | [7 empty] | -0.28
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 1.6 | [7 empty] | -0.34
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 1.8 | [7 empty] | -0.4
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.6 | 1 | [10 empty] | 2 | [7 empty] | -0.46
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 0.4 | [7 empty] | 0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 0.6 | [7 empty] | 0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 0.8 | [7 empty] | 0.05
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 1 | [7 empty] | 0.02
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 1.2 | [7 empty] | -0.03
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 1.4 | [7 empty] | -0.07
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 1.6 | [7 empty] | -0.12
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 1.8 | [7 empty] | -0.16
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 0.8 | 1 | [10 empty] | 2 | [7 empty] | -0.2
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 0.2 | [7 empty] | N/A
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 0.4 | [7 empty] | 0.09
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 0.6 | [7 empty] | 0.13
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 0.8 | [7 empty] | 0.13
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 1 | [7 empty] | 0.11
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 1.2 | [7 empty] | 0.08
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 1.4 | [7 empty] | 0.06
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 1.6 | [7 empty] | 0.03
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 1.8 | [7 empty] | -0.01
A10M | A-10 | Converging Junctions (Tees, Wyes) | CDEF | Rectangular | Case C, D, E & F Main Loss Coefficients | main | [52 empty] | 1 | 1 | [10 empty] | 2 | [7 empty] | -0.03
A10G | A-10 | Converging Junctions (Tees, Wyes) | G | Rectangular | Symmetrical Wye, Dovetail |  | input 1: Ab/Ac - select from list | 0.5 | [7 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [35 empty] | 0.5 | [16 empty] | 0.23
A10G | A-10 | Converging Junctions (Tees, Wyes) | G | Rectangular | Symmetrical Wye, Dovetail | [9 empty] | 1 | [46 empty] | 1 | [16 empty] | 0.07
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | H (in) | W_b (in) | W_s (in) | W_c (in) | Q_s (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.25 |  | 0.25 | [8 empty] | 0.1 | [8 empty] | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | H (mm) | W_b (mm) | W_s (mm) | W_c (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [44 empty] | 0.25 |  | 0.25 | [8 empty] | 0.2 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.3 | [8 empty] | 0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.4 | [8 empty] | 1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.5 | [8 empty] | 2.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.6 | [8 empty] | 3.7
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.7 | [8 empty] | 5.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.8 | [8 empty] | 8.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.9 | [8 empty] | 11
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.1 | [8 empty] | -1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.2 | [8 empty] | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.3 | [8 empty] | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.4 | [8 empty] | 1.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.5 | [8 empty] | 3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.6 | [8 empty] | 4.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.7 | [8 empty] | 6.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.8 | [8 empty] | 8.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.9 | [8 empty] | 11
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.1 | [8 empty] | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.2 | [8 empty] | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.3 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.4 | [8 empty] | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.5 | [8 empty] | 0.45
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.6 | [8 empty] | 0.7
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.7 | [8 empty] | 1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.8 | [8 empty] | 1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.9 | [8 empty] | 2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.1 | [8 empty] | -1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.2 | [8 empty] | -0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.3 | [8 empty] | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.4 | [8 empty] | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.5 | [8 empty] | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.6 | [8 empty] | 0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.7 | [8 empty] | 1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.8 | [8 empty] | 1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.9 | [8 empty] | 2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.1 | [8 empty] | -2.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.2 | [8 empty] | -1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.3 | [8 empty] | -0.95
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.4 | [8 empty] | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.8 | [8 empty] | 1.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.9 | [8 empty] | 1.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.1 | [8 empty] | -0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.2 | [8 empty] | -0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.3 | [8 empty] | -0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.4 | [8 empty] | -0.04
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0.13
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.21
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.29
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.8 | [8 empty] | 0.36
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.9 | [8 empty] | 0.42
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.1 | [8 empty] | -1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.2 | [8 empty] | -0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.3 | [8 empty] | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.4 | [8 empty] | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.5 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.6 | [8 empty] | 0.16
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.7 | [8 empty] | 0.24
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.8 | [8 empty] | 0.32
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.9 | [8 empty] | 0.38
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.1 | [8 empty] | -2.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.2 | [8 empty] | -1.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.3 | [8 empty] | -0.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.4 | [8 empty] | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.5 | [8 empty] | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.6 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.7 | [8 empty] | 0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.8 | [8 empty] | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.9 | [8 empty] | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [32 empty] | 0.25 | 0.75 | [9 empty] | 0.1 | [8 empty] | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.2 | [8 empty] | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.3 | [8 empty] | 0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.4 | [8 empty] | -0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.5 | [8 empty] | -0.45
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.6 | [8 empty] | -0.92
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.7 | [8 empty] | -1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.8 | [8 empty] | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.25 | 0.75 | [9 empty] | 0.9 | [8 empty] | -0.26
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.1 | [8 empty] | 0.17
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.2 | [8 empty] | 0.16
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.3 | [8 empty] | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.4 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.5 | [8 empty] | -0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.6 | [8 empty] | -0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.7 | [8 empty] | -0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.8 | [8 empty] | -0.37
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 1.05 | [9 empty] | 0.9 | [8 empty] | -0.46
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.1 | [8 empty] | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.2 | [8 empty] | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.3 | [8 empty] | 0.32
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.4 | [8 empty] | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.5 | [8 empty] | 0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.6 | [8 empty] | -0.03
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.7 | [8 empty] | -0.23
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.8 | [8 empty] | -0.42
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.75 | [9 empty] | 0.9 | [8 empty] | -0.58
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.1 | [8 empty] | 1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.2 | [8 empty] | 1.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.3 | [8 empty] | 0.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.4 | [8 empty] | 0.65
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.5 | [8 empty] | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.6 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.7 | [8 empty] | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.8 | [8 empty] | -0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 0.5 | 0.5 | [9 empty] | 0.9 | [8 empty] | -1.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.1 | [8 empty] | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.2 | [8 empty] | 0.24
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.3 | [8 empty] | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.4 | [8 empty] | 0.26
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.5 | [8 empty] | 0.23
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.6 | [8 empty] | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.7 | [8 empty] | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.8 | [8 empty] | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 1 | [9 empty] | 0.9 | [8 empty] | -0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.1 | [8 empty] | 0.75
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.2 | [8 empty] | 0.36
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.3 | [8 empty] | 0.38
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.4 | [8 empty] | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.5 | [8 empty] | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.6 | [8 empty] | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.7 | [8 empty] | 0.05
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.8 | [8 empty] | -0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.75 | [9 empty] | 0.9 | [8 empty] | -0.22
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.1 | [8 empty] | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.2 | [8 empty] | 0.87
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.3 | [8 empty] | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.4 | [8 empty] | 0.68
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.5 | [8 empty] | 0.55
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.6 | [8 empty] | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.7 | [8 empty] | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.8 | [8 empty] | 0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [52 empty] | 1 | 0.5 | [9 empty] | 0.9 | [8 empty] | -0.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye |  | D_branch | θ (degrees) - select from list | Q1b (cfm) | Q2b (cfm) | N/A | N/A | N/A | N/A |  | 15 | [6 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [46 empty] | 0 |  |  | 15 |  |  | -2.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye |  | D_branch | θ (degrees) - select from list | Q1b (m^3/hr) | Q2b (m^3/hr) | N/A | N/A | N/A | N/A |  | 30 | [56 empty] | 0 |  |  | 30 |  |  | -2.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [10 empty] | 45 | [56 empty] | 0 |  |  | 45 |  |  | -1.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.1 |  |  | 15 |  |  | -1.9
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.1 |  |  | 30 |  |  | -1.5
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.1 |  |  | 45 |  |  | -0.93
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.2 |  |  | 15 |  |  | -1.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.2 |  |  | 30 |  |  | -1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.2 |  |  | 45 |  |  | -0.55
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.3 |  |  | 15 |  |  | -0.77
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.3 |  |  | 30 |  |  | -0.53
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.3 |  |  | 45 |  |  | -0.16
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.4 |  |  | 15 |  |  | -0.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.4 |  |  | 30 |  |  | -0.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.4 |  |  | 45 |  |  | 0.2
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.5 |  |  | 15 |  |  | 0.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.5 |  |  | 30 |  |  | 0.28
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.5 |  |  | 45 |  |  | 0.56
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.6 |  |  | 15 |  |  | 0.41
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.6 |  |  | 30 |  |  | 0.69
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.6 |  |  | 45 |  |  | 0.92
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.7 |  |  | 15 |  |  | 0.67
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.7 |  |  | 30 |  |  | 0.91
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.7 |  |  | 45 |  |  | 1.26
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.8 |  |  | 15 |  |  | 0.85
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.8 |  |  | 30 |  |  | 1.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.8 |  |  | 45 |  |  | 1.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.9 |  |  | 15 |  |  | 0.97
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.9 |  |  | 30 |  |  | 1.4
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 0.9 |  |  | 45 |  |  | 2
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 1 |  |  | 15 |  |  | 1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 1 |  |  | 30 |  |  | 1.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [67 empty] | 1 |  |  | 45 |  |  | 2.3
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye |  | H | W_branch | θ (degrees) | Q1b (cfm) | Q2b (cfm) | N/A | N/A | N/A |  |  | 15 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [46 empty] | 0 |  |  | 15 |  |  | -2.6
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye |  | H | W_branch | θ (degrees) | Q1b (m^3/hr) | Q2b (m^3/hr) | N/A | N/A | N/A |  |  | 30 | [55 empty] | 0 |  |  | 30 |  |  | -2.1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [11 empty] | 45 | [55 empty] | 0 |  |  | 45 |  |  | -1.3
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.1 |  |  | 15 |  |  | -1.9
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.1 |  |  | 30 |  |  | -1.5
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.1 |  |  | 45 |  |  | -0.93
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.2 |  |  | 15 |  |  | -1.3
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.2 |  |  | 30 |  |  | -1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.2 |  |  | 45 |  |  | -0.55
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.3 |  |  | 15 |  |  | -0.77
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.3 |  |  | 30 |  |  | -0.53
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.3 |  |  | 45 |  |  | -0.16
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.4 |  |  | 15 |  |  | -0.3
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.4 |  |  | 30 |  |  | -0.1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.4 |  |  | 45 |  |  | 0.2
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.5 |  |  | 15 |  |  | 0.1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.5 |  |  | 30 |  |  | 0.28
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.5 |  |  | 45 |  |  | 0.56
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.6 |  |  | 15 |  |  | 0.41
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.6 |  |  | 30 |  |  | 0.69
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.6 |  |  | 45 |  |  | 0.92
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.7 |  |  | 15 |  |  | 0.67
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.7 |  |  | 30 |  |  | 0.91
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.7 |  |  | 45 |  |  | 1.26
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.8 |  |  | 15 |  |  | 0.85
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.8 |  |  | 30 |  |  | 1.1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.8 |  |  | 45 |  |  | 1.6
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.9 |  |  | 15 |  |  | 0.97
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.9 |  |  | 30 |  |  | 1.4
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 0.9 |  |  | 45 |  |  | 2
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 1 |  |  | 15 |  |  | 1
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 1 |  |  | 30 |  |  | 1.6
A10I2 | A-10 | Converging Junctions (Tees, Wyes) | I | Rectangular | Symmetrical Rectangular Wye | [67 empty] | 1 |  |  | 45 |  |  | 2.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | D_c (in) | D_b (in) | Angle - select from list | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [32 empty] | 0 | [13 empty] | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | D_c (mm) | D_b (mm) | Angle - select from list | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | [50 empty] | 0.1 | [13 empty] | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.2 | [13 empty] | 0.22
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.3 | [13 empty] | 0.17
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.4 | [13 empty] | 0.13
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.5 | [13 empty] | 0.09
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.6 | [13 empty] | 0.06
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 0.8 | [13 empty] | 0.02
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [58 empty] | 1 | [13 empty] | 0
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | D_c (in) | D_b (in) | Angle - select from list | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A |  |  | 30 | [5 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.8 | [10 empty] | 0.1 | [8 empty] | 0.75
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | D_c (mm) | D_b (mm) | Angle - select from list | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A |  |  | 45 | [41 empty] | 0.7 | [10 empty] | 0.1 | [8 empty] | 0.72
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [10 empty] | 60 | [41 empty] | 0.6 | [10 empty] | 0.1 | [8 empty] | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [10 empty] | 90 | [41 empty] | 0.5 | [10 empty] | 0.1 | [8 empty] | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.1 | [8 empty] | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.1 | [8 empty] | 0.55
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.1 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.1 | [8 empty] | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.2 | [8 empty] | 0.55
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.2 | [8 empty] | 0.51
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.2 | [8 empty] | 0.46
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.2 | [8 empty] | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.2 | [8 empty] | 0.33
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.2 | [8 empty] | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.2 | [8 empty] | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.3 | [8 empty] | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.3 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.3 | [8 empty] | 0.36
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.3 | [8 empty] | 0.31
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.3 | [8 empty] | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.3 | [8 empty] | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.3 | [8 empty] | 0.24
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.3 | [8 empty] | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.4 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.4 | [8 empty] | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.4 | [8 empty] | 0.25
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.4 | [8 empty] | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.4 | [8 empty] | 0.19
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.4 | [8 empty] | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.4 | [8 empty] | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.4 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.5 | [8 empty] | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.5 | [8 empty] | 0.18
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.5 | [8 empty] | 0.17
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.5 | [8 empty] | 0.18
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.5 | [8 empty] | 0.27
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.5 | [8 empty] | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.5 | [8 empty] | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.6 | [8 empty] | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.6 | [8 empty] | 0.15
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.6 | [8 empty] | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.6 | [8 empty] | 0.22
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.6 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.6 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.7 | [8 empty] | 0.15
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.7 | [8 empty] | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.7 | [8 empty] | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.7 | [8 empty] | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.7 | [8 empty] | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.7 | [8 empty] | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.8 | [8 empty] | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.8 | [8 empty] | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.8 | [8 empty] | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.8 | [8 empty] | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.8 | [8 empty] | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.8 | [10 empty] | 0.9 | [8 empty] | 0.19
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.7 | [10 empty] | 0.9 | [8 empty] | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.6 | [10 empty] | 0.9 | [8 empty] | 0.39
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.5 | [10 empty] | 0.9 | [8 empty] | 0.67
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.4 | [10 empty] | 0.9 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.3 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.2 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.8 | [10 empty] | 0.1 | [8 empty] | 0.78
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [44 empty] | 0.7 | [10 empty] | 0.1 | [8 empty] | 0.77
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.1 | [8 empty] | 0.74
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.1 | [8 empty] | 0.71
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.1 | [8 empty] | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.1 | [8 empty] | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.1 | [8 empty] | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.1 | [8 empty] | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.2 | [8 empty] | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.2 | [8 empty] | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.2 | [8 empty] | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.2 | [8 empty] | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.2 | [8 empty] | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.2 | [8 empty] | 0.48
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.2 | [8 empty] | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.3 | [8 empty] | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.3 | [8 empty] | 0.49
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.3 | [8 empty] | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.3 | [8 empty] | 0.44
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.3 | [8 empty] | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.3 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.3 | [8 empty] | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.3 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.4 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.4 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.4 | [8 empty] | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.4 | [8 empty] | 0.37
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.4 | [8 empty] | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.4 | [8 empty] | 0.43
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.4 | [8 empty] | 0.73
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.4 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.5 | [8 empty] | 0.34
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.5 | [8 empty] | 0.34
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.5 | [8 empty] | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.5 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.5 | [8 empty] | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.5 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.6 | [8 empty] | 0.31
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.6 | [8 empty] | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.6 | [8 empty] | 0.36
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.6 | [8 empty] | 0.45
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.6 | [8 empty] | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.6 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.7 | [8 empty] | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.7 | [8 empty] | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.7 | [8 empty] | 0.43
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.7 | [8 empty] | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.7 | [8 empty] | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.7 | [8 empty] | 2.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.8 | [8 empty] | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.8 | [8 empty] | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.8 | [8 empty] | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.8 | [8 empty] | 0.78
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.8 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.8 | [10 empty] | 0.9 | [8 empty] | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.7 | [10 empty] | 0.9 | [8 empty] | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.6 | [10 empty] | 0.9 | [8 empty] | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.5 | [10 empty] | 0.9 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.4 | [10 empty] | 0.9 | [8 empty] | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.3 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.2 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.8 | [10 empty] | 0.1 | [8 empty] | 0.83
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [44 empty] | 0.7 | [10 empty] | 0.1 | [8 empty] | 0.82
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.1 | [8 empty] | 0.81
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.1 | [8 empty] | 0.79
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.1 | [8 empty] | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.1 | [8 empty] | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.1 | [8 empty] | 0.77
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.1 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.2 | [8 empty] | 0.71
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.2 | [8 empty] | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.2 | [8 empty] | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.2 | [8 empty] | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.2 | [8 empty] | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.2 | [8 empty] | 0.75
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.2 | [8 empty] | 0.96
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.3 | [8 empty] | 2.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.3 | [8 empty] | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.3 | [8 empty] | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.3 | [8 empty] | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.3 | [8 empty] | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.3 | [8 empty] | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.3 | [8 empty] | 0.89
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.3 | [8 empty] | 1.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.4 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.4 | [8 empty] | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.4 | [8 empty] | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.4 | [8 empty] | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.4 | [8 empty] | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.4 | [8 empty] | 0.74
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.4 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.4 | [8 empty] | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.5 | [8 empty] | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.5 | [8 empty] | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.5 | [8 empty] | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.5 | [8 empty] | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.5 | [8 empty] | 0.89
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.5 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.6 | [8 empty] | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.6 | [8 empty] | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.6 | [8 empty] | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.6 | [8 empty] | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.6 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.6 | [8 empty] | 2.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.7 | [8 empty] | 0.53
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.7 | [8 empty] | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.7 | [8 empty] | 0.72
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.7 | [8 empty] | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.7 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.7 | [8 empty] | 3.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.8 | [8 empty] | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.8 | [8 empty] | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.8 | [8 empty] | 0.87
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.8 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.8 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.8 | [10 empty] | 0.9 | [8 empty] | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.7 | [10 empty] | 0.9 | [8 empty] | 0.82
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.6 | [10 empty] | 0.9 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.5 | [10 empty] | 0.9 | [8 empty] | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.4 | [10 empty] | 0.9 | [8 empty] | 2.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.3 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.2 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.8 | [10 empty] | 0.1 | [8 empty] | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [44 empty] | 0.7 | [10 empty] | 0.1 | [8 empty] | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.1 | [8 empty] | 0.96
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.1 | [8 empty] | 0.97
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.1 | [8 empty] | 0.99
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.1 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.1 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.1 | [8 empty] | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.2 | [8 empty] | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.2 | [8 empty] | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.2 | [8 empty] | 0.97
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.2 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.2 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.2 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.2 | [8 empty] | 1.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.3 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.3 | [8 empty] | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.3 | [8 empty] | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.3 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.3 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.3 | [8 empty] | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.3 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.3 | [8 empty] | 2.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.4 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.4 | [8 empty] | 0.93
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.4 | [8 empty] | 0.98
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.4 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.4 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.4 | [8 empty] | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.4 | [8 empty] | 2.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.4 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.5 | [8 empty] | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.5 | [8 empty] | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.5 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.5 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.5 | [8 empty] | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.5 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.6 | [8 empty] | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.6 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.6 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.6 | [8 empty] | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.6 | [8 empty] | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.6 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.7 | [8 empty] | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.7 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.7 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.7 | [8 empty] | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.7 | [8 empty] | 2.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.7 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.8 | [8 empty] | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.8 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.8 | [8 empty] | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.8 | [8 empty] | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.8 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.8 | [10 empty] | 0.9 | [8 empty] | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.7 | [10 empty] | 0.9 | [8 empty] | 1.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.6 | [10 empty] | 0.9 | [8 empty] | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.5 | [10 empty] | 0.9 | [8 empty] | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.4 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.3 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.2 | [10 empty] | 0.9 | [8 empty] | N/A
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [52 empty] | 0.1 | [10 empty] | 0.9 | [8 empty] | N/A
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.85
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 0.4 | [14 empty] | 0.74
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 0.6 | [14 empty] | 0.62
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 0.8 | [14 empty] | 0.52
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 1 | [14 empty] | 0.42
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 1.2 | [14 empty] | 0.36
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 1.4 | [14 empty] | 0.32
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 1.6 | [14 empty] | 0.32
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 1.8 | [14 empty] | 0.37
A11B | A-11 | Diverging Junctions (Tees, Wyes) | B | Round | Conical Tee, 90° | branch | [57 empty] | 2 | [14 empty] | 0.52
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.84
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 0.4 | [14 empty] | 0.61
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 0.6 | [14 empty] | 0.41
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 0.8 | [14 empty] | 0.27
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 1 | [14 empty] | 0.17
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 1.2 | [14 empty] | 0.12
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 1.4 | [14 empty] | 0.12
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 1.6 | [14 empty] | 0.14
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 1.8 | [14 empty] | 0.18
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [57 empty] | 2 | [14 empty] | 0.27
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 1.32
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.4 | [14 empty] | 1.51
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 1.6
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 1.65
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 1.74
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 1.87
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 2
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 2.2
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 2.5
A11D | A-11 | Diverging Junctions (Tees, Wyes) | D | Round | 90° Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 2.7
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 1.03
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 0.4 | [14 empty] | 1.08
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 1.18
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 1.33
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 1.56
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 1.86
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 2.2
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 2.6
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 3
A11E | A-11 | Diverging Junctions (Tees, Wyes) | E | Round | 90° Tee, with 90° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 3.4
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 1.06
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.4 | [14 empty] | 1.15
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.6 | [14 empty] | 1.29
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.8 | [14 empty] | 1.45
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1 | [14 empty] | 1.65
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.2 | [14 empty] | 1.89
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.4 | [14 empty] | 2.2
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.6 | [14 empty] | 2.5
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.8 | [14 empty] | 2.9
A11F | A-11 | Diverging Junctions (Tees, Wyes) | F | Round | 90° Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 2 | [14 empty] | 3.3
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.94
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.88
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.84
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.8
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 0.82
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.84
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.87
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 0.9
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 0.95
A11G | A-11 | Diverging Junctions (Tees, Wyes) | G | Round | 90° Conical Tee, Rolled 45° with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 1.02
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.95
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.9
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.86
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.81
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1 | [14 empty] | 0.79
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.79
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.81
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.6 | [14 empty] | 0.86
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 1.8 | [14 empty] | 0.96
A11H | A-11 | Diverging Junctions (Tees, Wyes) | H | Round | 90° Conical Tee, Rolled 45° with 60° Elbow, Branch 45° to Main | branch | [57 empty] | 2 | [14 empty] | 1.1
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.88
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.77
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.68
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.65
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 0.69
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.73
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.88
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 1.14
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 1.54
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 2.2
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.82
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.63
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.52
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.45
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 0.42
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.41
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.4
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 0.41
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 0.45
A11J | A-11 | Diverging Junctions (Tees, Wyes) | J | Round | 45° Conical Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 0.56
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.84
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.72
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.62
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.54
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1 | [14 empty] | 0.5
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.56
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.71
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.6 | [14 empty] | 0.92
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.8 | [14 empty] | 1.22
A11K | A-11 | Diverging Junctions (Tees, Wyes) | K | Round | 45° Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 2 | [14 empty] | 1.66
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0 | [14 empty] | 1
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | N/A | [49 empty] | 0.2 | [14 empty] | 0.93
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.4 | [14 empty] | 0.71
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.55
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.44
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1 | [14 empty] | 0.42
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.42
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.44
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.6 | [14 empty] | 0.47
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 1.8 | [14 empty] | 0.54
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [57 empty] | 2 | [14 empty] | 0.62
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | D_s (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [14 empty] | 0.76
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | D_s (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | [49 empty] | 0.4 | [14 empty] | 0.6
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.6 | [14 empty] | 0.52
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.7 | [14 empty] | 0.5
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.8 | [14 empty] | 0.51
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 0.9 | [14 empty] | 0.52
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1 | [14 empty] | 0.56
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.1 | [14 empty] | 0.61
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.2 | [14 empty] | 0.68
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.4 | [14 empty] | 0.86
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.6 | [14 empty] | 1.1
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 1.8 | [14 empty] | 1.4
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2 | [14 empty] | 1.8
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2.2 | [14 empty] | 2.2
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2.4 | [14 empty] | 2.6
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2.6 | [14 empty] | 3.1
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 2.8 | [14 empty] | 3.7
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [57 empty] | 3 | [14 empty] | 4.2
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 0.2 | [13 empty] | 0.14
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 0.4 | [13 empty] | 0.06
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 0.6 | [13 empty] | 0.05
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 0.8 | [13 empty] | 0.09
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 1 | [13 empty] | 0.18
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 1.2 | [13 empty] | 0.3
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 1.4 | [13 empty] | 0.46
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 1.6 | [13 empty] | 0.64
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 1.8 | [13 empty] | 0.84
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [58 empty] | 2 | [13 empty] | 1
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 0.91
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 0.81
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 0.77
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 0.78
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 0.78
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 1.19
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 1.35
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 1.44
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.2 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 0.79
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 0.72
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 0.73
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 0.98
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 1.11
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 1.22
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 1.42
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 1.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.3 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.3 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 0.69
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 0.85
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 1.16
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 1.26
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 1.55
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 1.75
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.4 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.4 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.4 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 0.66
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 0.79
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 1.23
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 1.29
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 1.59
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 1.74
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.5 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.5 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.5 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.5 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 0.74
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.03
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 1.54
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 1.63
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 1.72
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.6 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.6 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.6 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.6 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.6 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 0.86
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 1.25
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 1.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 2.24
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 0.92
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 1.31
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 1.63
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 1.09
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 1.4
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 1.17
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 0.61
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 0.46
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 0.43
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 0.39
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 0.34
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 0.37
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 0.57
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 0.89
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 1.33
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.2 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 0.61
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 0.43
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 0.57
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 0.64
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 0.71
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 1.08
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 1.34
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.3 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.3 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 0.54
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 0.62
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 0.77
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 0.85
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 1.04
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 1.28
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 2.04
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.4 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.4 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.4 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 0.53
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 0.73
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 0.98
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 1.16
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 1.3
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 1.78
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.5 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.5 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.5 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.5 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 0.68
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.07
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 1.54
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 1.69
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 1.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.6 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.6 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.6 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.6 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.6 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 0.83
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 1.36
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 2.09
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 2.4
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 1.18
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 1.81
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 2.77
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 1.47
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 2.23
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 1.92
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 1.03
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 1.04
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 1.11
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 1.16
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 1.38
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 1.52
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 1.79
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 2.07
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 2.32
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.2 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 1.01
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 1.03
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 1.21
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 1.4
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 1.61
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 2.01
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 2.28
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 2.54
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.3 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.3 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 1.05
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 1.17
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 1.3
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 1.68
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 1.9
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 2.13
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 2.64
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.4 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.4 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.4 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 1.12
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 1.36
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 1.91
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 2.31
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 2.71
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 3.09
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.5 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.5 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.5 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.5 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 1.27
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.47
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 2.28
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 2.99
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 3.72
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.6 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.6 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.6 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.6 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.6 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 1.66
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 2.2
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 2.81
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 3.48
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 1.95
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 2.09
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 2.21
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 2.2
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 2.29
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11P | A-11 | Diverging Junctions (Tees, Wyes) | P | Rectangular | Tee Rectangular Main & Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 2.57
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 0.58
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 0.67
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 0.78
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 0.88
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 1.12
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 1.49
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 2.1
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 2.72
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 3.42
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.2 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 0.64
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 0.76
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 0.98
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 1.05
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 1.48
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 2.21
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 3.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 4.58
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.3 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.3 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 0.75
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 0.81
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 1.08
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 1.4
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 2.25
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 2.84
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 3.65
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.4 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.4 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.4 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 1.01
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 1.18
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 1.51
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 2.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 3.09
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 3.92
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.5 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.5 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.5 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.5 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 1.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 2.32
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 3.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 4.2
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.6 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.6 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.6 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.6 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.6 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 1.91
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 2.48
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 3.19
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 4.15
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 2.53
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 3.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 4.14
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 3.16
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 4.1
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 0.8 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 4.05
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 0.62
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 0.74
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 0.99
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 1.48
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 1.91
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 2.47
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 3.17
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 3.85
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.2 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 0.69
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 1.1
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 1.12
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 1.33
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 1.67
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 2.4
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 3.37
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.3 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.3 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 0.82
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 0.95
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 1.41
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 1.43
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 1.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 2.33
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 2.89
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.4 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.4 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.4 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 1.24
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 1.52
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 2.04
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 2.53
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 3.23
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.5 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.5 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.5 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.5 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 1.21
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.55
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 1.86
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 2.31
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 3.09
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.6 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.6 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.6 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.6 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.6 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 1.64
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 1.98
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 2.51
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 3.03
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.7 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 2.47
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 3.13
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 3.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.8 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 3.25
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 3.74
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 0.8 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.2 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.4 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.6 | [5 empty] | 0.9 | [8 empty] | N/A
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 4.11
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [37 empty] | 0.2 | [14 empty] | 0.03
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 0.4 | [14 empty] | 0.04
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 0.6 | [14 empty] | 0.07
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 0.8 | [14 empty] | 0.12
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 1 | [14 empty] | 0.13
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 1.2 | [14 empty] | 0.14
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 1.4 | [14 empty] | 0.27
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 1.6 | [14 empty] | 0.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [57 empty] | 1.8 | [14 empty] | 0.25
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | H_c (in) | W_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.2 | [5 empty] | 0.1 | [8 empty] | 1
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | H_c (mm) | W_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | [49 empty] | 0.4 | [5 empty] | 0.1 | [8 empty] | 1.01
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.1 | [8 empty] | 1.14
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.1 | [8 empty] | 1.18
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.1 | [8 empty] | 1.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.1 | [8 empty] | 1.46
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.1 | [8 empty] | 1.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.1 | [8 empty] | 1.93
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.1 | [8 empty] | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.2 | [8 empty] | 1.07
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.2 | [8 empty] | 1.1
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.2 | [8 empty] | 1.31
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.2 | [8 empty] | 1.38
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.2 | [8 empty] | 1.58
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.2 | [8 empty] | 1.82
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.2 | [8 empty] | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.2 | [8 empty] | 2.17
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.3 | [8 empty] | 1.08
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.3 | [8 empty] | 1.12
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.3 | [8 empty] | 1.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.3 | [8 empty] | 1.45
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.3 | [8 empty] | 1.65
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.3 | [8 empty] | 2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.3 | [8 empty] | 2.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.4 | [8 empty] | 1.13
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.4 | [8 empty] | 1.23
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.4 | [8 empty] | 1.31
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.4 | [8 empty] | 1.51
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.4 | [8 empty] | 1.85
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.4 | [8 empty] | 2.13
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.5 | [8 empty] | 1.26
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.5 | [8 empty] | 1.39
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.5 | [8 empty] | 1.56
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.5 | [8 empty] | 1.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.5 | [8 empty] | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.6 | [8 empty] | 1.48
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.6 | [8 empty] | 1.64
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.6 | [8 empty] | 1.76
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.6 | [8 empty] | 1.98
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.7 | [8 empty] | 1.71
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.7 | [8 empty] | 1.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.7 | [8 empty] | 1.99
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.8 | [8 empty] | 1.88
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.8 | [8 empty] | 2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.2 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.4 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.6 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 0.8 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.2 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.4 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.6 | [5 empty] | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [57 empty] | 1.8 | [5 empty] | 0.9 | [8 empty] | 2.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | H (in) | W_c (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Angle | [7 empty] | 15 |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [37 empty] | 0.1 | [11 empty] | 15 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [13 empty] | 30 | [43 empty] | 0.1 | [11 empty] | 30 |  |  | 0.84
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [13 empty] | 45 | [43 empty] | 0.1 | [11 empty] | 45 |  |  | 0.87
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [13 empty] | 60 | [43 empty] | 0.1 | [11 empty] | 60 |  |  | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [13 empty] | 90 | [43 empty] | 0.1 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.2 | [11 empty] | 15 |  |  | 0.65
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.2 | [11 empty] | 30 |  |  | 0.69
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.2 | [11 empty] | 45 |  |  | 0.74
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.2 | [11 empty] | 60 |  |  | 0.82
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.2 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.3 | [11 empty] | 15 |  |  | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.3 | [11 empty] | 30 |  |  | 0.56
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.3 | [11 empty] | 45 |  |  | 0.63
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.3 | [11 empty] | 60 |  |  | 0.79
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.3 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.4 | [11 empty] | 15 |  |  | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.4 | [11 empty] | 30 |  |  | 0.44
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.4 | [11 empty] | 45 |  |  | 0.54
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.4 | [11 empty] | 60 |  |  | 0.66
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.4 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.5 | [11 empty] | 15 |  |  | 0.28
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.5 | [11 empty] | 30 |  |  | 0.34
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.5 | [11 empty] | 45 |  |  | 0.45
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.5 | [11 empty] | 60 |  |  | 0.59
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.5 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.6 | [11 empty] | 15 |  |  | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.6 | [11 empty] | 30 |  |  | 0.26
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.6 | [11 empty] | 45 |  |  | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.6 | [11 empty] | 60 |  |  | 0.53
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.6 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.8 | [11 empty] | 15 |  |  | 0.11
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.8 | [11 empty] | 30 |  |  | 0.19
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.8 | [11 empty] | 45 |  |  | 0.29
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.8 | [11 empty] | 60 |  |  | 0.43
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 0.8 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1 | [11 empty] | 15 |  |  | 0.06
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1 | [11 empty] | 30 |  |  | 0.15
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1 | [11 empty] | 45 |  |  | 0.24
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1 | [11 empty] | 60 |  |  | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.2 | [11 empty] | 15 |  |  | 0.14
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.2 | [11 empty] | 30 |  |  | 0.15
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.2 | [11 empty] | 45 |  |  | 0.23
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.2 | [11 empty] | 60 |  |  | 0.33
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.2 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.4 | [11 empty] | 15 |  |  | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.4 | [11 empty] | 30 |  |  | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.4 | [11 empty] | 45 |  |  | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.4 | [11 empty] | 60 |  |  | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.4 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.6 | [11 empty] | 15 |  |  | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.6 | [11 empty] | 30 |  |  | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.6 | [11 empty] | 45 |  |  | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.6 | [11 empty] | 60 |  |  | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.6 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.8 | [11 empty] | 15 |  |  | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.8 | [11 empty] | 30 |  |  | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.8 | [11 empty] | 45 |  |  | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.8 | [11 empty] | 60 |  |  | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 1.8 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 2 | [11 empty] | 15 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 2 | [11 empty] | 30 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 2 | [11 empty] | 45 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 2 | [11 empty] | 60 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [57 empty] | 2 | [11 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [33 empty] | 0 - 1.0 |  |  |  |  | 0 | [10 empty] | 15-60 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.1 | [10 empty] | 15-60 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.2 | [10 empty] | 15-60 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.3 | [10 empty] | 15-60 |  |  | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.4 | [10 empty] | 15-60 |  |  | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.5 | [10 empty] | 15-60 |  |  | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.6 | [10 empty] | 15-60 |  |  | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 0.8 | [10 empty] | 15-60 |  |  | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 1 | [10 empty] | 15-60 |  |  | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 1.2 | [10 empty] | 15-60 |  |  | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 1.4 | [10 empty] | 15-60 |  |  | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 1.6 | [10 empty] | 15-60 |  |  | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 1.8 | [10 empty] | 15-60 |  |  | 1.8
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 1.0 |  |  |  |  | 2 | [10 empty] | 15-60 |  |  | 3.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0 | [10 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.1 | [10 empty] | 90 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.2 | [10 empty] | 90 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.3 | [10 empty] | 90 |  |  | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.4 | [10 empty] | 90 |  |  | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.5 | [10 empty] | 90 |  |  | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.6 | [10 empty] | 90 |  |  | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 0.8 | [10 empty] | 90 |  |  | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 1 | [10 empty] | 90 |  |  | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 1.2 | [10 empty] | 90 |  |  | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 1.4 | [10 empty] | 90 |  |  | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 1.6 | [10 empty] | 90 |  |  | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 1.8 | [10 empty] | 90 |  |  | 1.8
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0 - 0.4 |  |  |  |  | 2 | [10 empty] | 90 |  |  | 3.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0 | [10 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.1 | [10 empty] | 90 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.2 | [10 empty] | 90 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.3 | [10 empty] | 90 |  |  | 0.52
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.4 | [10 empty] | 90 |  |  | 0.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.5 | [10 empty] | 90 |  |  | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.6 | [10 empty] | 90 |  |  | 0.23
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 0.8 | [10 empty] | 90 |  |  | 0.17
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 1 | [10 empty] | 90 |  |  | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 1.2 | [10 empty] | 90 |  |  | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 1.4 | [10 empty] | 90 |  |  | 0.79
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 1.6 | [10 empty] | 90 |  |  | 1.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 1.8 | [10 empty] | 90 |  |  | 2.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.5 |  |  |  |  | 2 | [10 empty] | 90 |  |  | 4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0 | [10 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.1 | [10 empty] | 90 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.2 | [10 empty] | 90 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.3 | [10 empty] | 90 |  |  | 0.52
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.4 | [10 empty] | 90 |  |  | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.5 | [10 empty] | 90 |  |  | 0.28
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.6 | [10 empty] | 90 |  |  | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 0.8 | [10 empty] | 90 |  |  | 0.1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 1 | [10 empty] | 90 |  |  | 0.1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 1.2 | [10 empty] | 90 |  |  | 0.21
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 1.4 | [10 empty] | 90 |  |  | 0.59
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 1.6 | [10 empty] | 90 |  |  | 1.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 1.8 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.6 |  |  |  |  | 2 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0 | [10 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.1 | [10 empty] | 90 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.2 | [10 empty] | 90 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.3 | [10 empty] | 90 |  |  | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.4 | [10 empty] | 90 |  |  | 0.37
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.5 | [10 empty] | 90 |  |  | 0.27
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.6 | [10 empty] | 90 |  |  | 0.18
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 0.8 | [10 empty] | 90 |  |  | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 1 | [10 empty] | 90 |  |  | 0.05
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 1.2 | [10 empty] | 90 |  |  | 0.14
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 1.4 | [10 empty] | 90 |  |  | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 1.6 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 1.8 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | 0.7 |  |  |  |  | 2 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0 | [10 empty] | 90 |  |  | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.1 | [10 empty] | 90 |  |  | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.2 | [10 empty] | 90 |  |  | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.3 | [10 empty] | 90 |  |  | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.4 | [10 empty] | 90 |  |  | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.5 | [10 empty] | 90 |  |  | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.6 | [10 empty] | 90 |  |  | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 0.8 | [10 empty] | 90 |  |  | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 1 | [10 empty] | 90 |  |  | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 1.2 | [10 empty] | 90 |  |  | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 1.4 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 1.6 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 1.8 | [10 empty] | 90 |  |  | N/A
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [53 empty] | >=0.8 |  |  |  |  | 2 | [10 empty] | 90 |  |  | N/A
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | H (in) | W (in) | D (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [31 empty] | 0.4 | [14 empty] | 0.8
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | H (mm) | W (mm) | D (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | N/A | [49 empty] | 0.5 | [14 empty] | 0.83
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | [57 empty] | 0.75 | [14 empty] | 0.9
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | [57 empty] | 1 | [14 empty] | 1
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | [57 empty] | 1.3 | [14 empty] | 1.1
A11U | A-11 | Diverging Junctions (Tees, Wyes) | U | Rectangular | Tee Rectangular Main to Conical Branch | branch | [57 empty] | 1.5 | [14 empty] | 1.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | H (in) | W_c (in) | W_b (in) | W_s (in) | Q_c (cfm) | Q_b (cfm) | N/A | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [26 empty] | 0.25 |  | 0.25 | [8 empty] | 0.1 | [8 empty] | 0.55
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | H (mm) | W_c (mm) | W_b (mm) | W_s (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | N/A | N/A | [44 empty] | 0.25 |  | 0.33 | [8 empty] | 0.1 | [8 empty] | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.1 | [8 empty] | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.1 | [8 empty] | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.1 | [8 empty] | 0.44
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.1 | [8 empty] | 0.67
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.1 | [8 empty] | 0.7
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.1 | [8 empty] | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.2 | [8 empty] | 0.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.2 | [8 empty] | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.2 | [8 empty] | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.2 | [8 empty] | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.2 | [8 empty] | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.2 | [8 empty] | 0.55
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.2 | [8 empty] | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.2 | [8 empty] | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.3 | [8 empty] | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.3 | [8 empty] | 0.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.3 | [8 empty] | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.3 | [8 empty] | 0.32
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.3 | [8 empty] | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.3 | [8 empty] | 0.46
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.3 | [8 empty] | 0.51
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.3 | [8 empty] | 0.43
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.4 | [8 empty] | 0.85
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.4 | [8 empty] | 0.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.4 | [8 empty] | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.4 | [8 empty] | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.4 | [8 empty] | 0.41
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.4 | [8 empty] | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.4 | [8 empty] | 0.42
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.4 | [8 empty] | 0.33
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.5 | [8 empty] | 1.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.5 | [8 empty] | 1.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.5 | [8 empty] | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.5 | [8 empty] | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0.32
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.5 | [8 empty] | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.5 | [8 empty] | 0.24
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.6 | [8 empty] | 1.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.6 | [8 empty] | 2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.6 | [8 empty] | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.6 | [8 empty] | 0.44
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.68
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.6 | [8 empty] | 0.28
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.6 | [8 empty] | 0.17
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.7 | [8 empty] | 3.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.7 | [8 empty] | 2.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.7 | [8 empty] | 0.78
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.7 | [8 empty] | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.92
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.7 | [8 empty] | 0.26
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.7 | [8 empty] | 0.15
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.8 | [8 empty] | 4.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.8 | [8 empty] | 3.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.8 | [8 empty] | 1.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.8 | [8 empty] | 0.92
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.8 | [8 empty] | 1.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.8 | [8 empty] | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.8 | [8 empty] | 0.26
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.8 | [8 empty] | 0.17
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.9 | [8 empty] | 6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.9 | [8 empty] | 5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.9 | [8 empty] | 1.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.9 | [8 empty] | 1.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.9 | [8 empty] | 1.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1 | [8 empty] | 0.9 | [8 empty] | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.9 | [8 empty] | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [52 empty] | 1 |  | 2 | [8 empty] | 0.9 | [8 empty] | 0.21
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [32 empty] | 0.25 |  | 0.25 | [8 empty] | 0.1 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.1 | [8 empty] | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.1 | [8 empty] | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.1 | [8 empty] | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.1 | [8 empty] | 0.72
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.1 | [8 empty] | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.1 | [8 empty] | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.1 | [8 empty] | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.2 | [8 empty] | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.2 | [8 empty] | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.2 | [8 empty] | -0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.2 | [8 empty] | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.2 | [8 empty] | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.2 | [8 empty] | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.2 | [8 empty] | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.2 | [8 empty] | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.3 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.3 | [8 empty] | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.3 | [8 empty] | -0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.3 | [8 empty] | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.3 | [8 empty] | 0.28
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.3 | [8 empty] | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.3 | [8 empty] | 0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.3 | [8 empty] | 0.23
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.4 | [8 empty] | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.4 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.4 | [8 empty] | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.4 | [8 empty] | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.4 | [8 empty] | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.4 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.4 | [8 empty] | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.4 | [8 empty] | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.5 | [8 empty] | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.5 | [8 empty] | 0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.5 | [8 empty] | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.5 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.5 | [8 empty] | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.5 | [8 empty] | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.5 | [8 empty] | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.6 | [8 empty] | 0.21
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.6 | [8 empty] | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.6 | [8 empty] | 0.12
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.6 | [8 empty] | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.6 | [8 empty] | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.6 | [8 empty] | 0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.6 | [8 empty] | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.7 | [8 empty] | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.7 | [8 empty] | 0.16
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.7 | [8 empty] | 0.19
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.7 | [8 empty] | 0.12
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.09
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.7 | [8 empty] | 0.22
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.7 | [8 empty] | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.7 | [8 empty] | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.8 | [8 empty] | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.8 | [8 empty] | 0.24
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.8 | [8 empty] | 0.27
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.8 | [8 empty] | 0.23
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.8 | [8 empty] | 0.18
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.8 | [8 empty] | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.8 | [8 empty] | 0.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.8 | [8 empty] | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.25 | [8 empty] | 0.9 | [8 empty] | 0.46
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.25 |  | 0.33 | [8 empty] | 0.9 | [8 empty] | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.5 | [8 empty] | 0.9 | [8 empty] | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 0.67 | [8 empty] | 0.9 | [8 empty] | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 0.5 |  | 1 | [8 empty] | 0.9 | [8 empty] | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1 | [8 empty] | 0.9 | [8 empty] | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 1.33 | [8 empty] | 0.9 | [8 empty] | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [52 empty] | 1 |  | 2 | [8 empty] | 0.9 | [8 empty] | 0.2
A11W | A-11 | Diverging Junctions (Tees, Wyes) | W | Rectangular | Symmetrical Wye Dovetail |  | input 1: H (in); input 2: W_c (in); input 3: branch area/main area; input 4: Qc (cfm) |  |  | 0.5 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [35 empty] | 0.5 | [16 empty] | 0.3
A11W | A-11 | Diverging Junctions (Tees, Wyes) | W | Rectangular | Symmetrical Wye Dovetail | [11 empty] | 1 | [44 empty] | 1 | [16 empty] | 0.25
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round |  | H (in) | W_c (in) | θ (degrees) | Qb1 (cfm) | Qb2 (cfm) | N/A | N/A | N/A |  |  | 15 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [39 empty] | 0.1 | [9 empty] | 15 |  |  | 0.81
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round |  | H (mm) | W_c (mm) | θ (degrees) | Qb1 (m^3/hr) | Qb2 (m^3/hr) | N/A | N/A | N/A |  |  | 30 | [48 empty] | 0.1 | [9 empty] | 30 |  |  | 0.84
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [11 empty] | 45 | [48 empty] | 0.1 | [9 empty] | 45 |  |  | 0.87
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [11 empty] | 60 | [48 empty] | 0.1 | [9 empty] | 60 |  |  | 0.9
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [11 empty] | 90 | [48 empty] | 0.1 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.2 | [9 empty] | 15 |  |  | 0.65
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.2 | [9 empty] | 30 |  |  | 0.69
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.2 | [9 empty] | 45 |  |  | 0.74
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.2 | [9 empty] | 60 |  |  | 0.82
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.2 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.3 | [9 empty] | 15 |  |  | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.3 | [9 empty] | 30 |  |  | 0.56
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.3 | [9 empty] | 45 |  |  | 0.63
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.3 | [9 empty] | 60 |  |  | 0.79
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.3 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.4 | [9 empty] | 15 |  |  | 0.38
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.4 | [9 empty] | 30 |  |  | 0.44
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.4 | [9 empty] | 45 |  |  | 0.54
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.4 | [9 empty] | 60 |  |  | 0.66
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.4 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.5 | [9 empty] | 15 |  |  | 0.28
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.5 | [9 empty] | 30 |  |  | 0.34
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.5 | [9 empty] | 45 |  |  | 0.45
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.5 | [9 empty] | 60 |  |  | 0.59
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.5 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.6 | [9 empty] | 15 |  |  | 0.2
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.6 | [9 empty] | 30 |  |  | 0.26
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.6 | [9 empty] | 45 |  |  | 0.38
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.6 | [9 empty] | 60 |  |  | 0.53
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.6 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.8 | [9 empty] | 15 |  |  | 0.11
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.8 | [9 empty] | 30 |  |  | 0.19
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.8 | [9 empty] | 45 |  |  | 0.29
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.8 | [9 empty] | 60 |  |  | 0.43
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 0.8 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1 | [9 empty] | 15 |  |  | 0.06
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1 | [9 empty] | 30 |  |  | 0.15
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1 | [9 empty] | 45 |  |  | 0.24
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1 | [9 empty] | 60 |  |  | 0.36
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.2 | [9 empty] | 15 |  |  | 0.14
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.2 | [9 empty] | 30 |  |  | 0.15
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.2 | [9 empty] | 45 |  |  | 0.23
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.2 | [9 empty] | 60 |  |  | 0.36
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.2 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.4 | [9 empty] | 15 |  |  | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.4 | [9 empty] | 30 |  |  | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.4 | [9 empty] | 45 |  |  | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.4 | [9 empty] | 60 |  |  | 0.39
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.4 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.6 | [9 empty] | 15 |  |  | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.6 | [9 empty] | 30 |  |  | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.6 | [9 empty] | 45 |  |  | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.6 | [9 empty] | 60 |  |  | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.6 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.8 | [9 empty] | 15 |  |  | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.8 | [9 empty] | 30 |  |  | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.8 | [9 empty] | 45 |  |  | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.8 | [9 empty] | 60 |  |  | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 1.8 | [9 empty] | 90 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 2 | [9 empty] | 15 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 2 | [9 empty] | 30 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 2 | [9 empty] | 45 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 2 | [9 empty] | 60 |  |  | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [60 empty] | 2 | [9 empty] | 90 |  |  | 1
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Q_s (cfm) | N/A | [8 empty] | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | #REF! | Vel Pres. at Vₒ (Pv, in. wc) | [37 empty] | 0.1 | [8 empty] | 1.16
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | Q_s (m^3/hr) | N/A | [55 empty] | 0.2 | [8 empty] | 0.96
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.3 | [8 empty] | 0.82
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.4 | [8 empty] | 0.68
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.5 | [8 empty] | 0.56
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.6 | [8 empty] | 0.49
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.7 | [8 empty] | 0.47
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.8 | [8 empty] | 0.48
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 0.9 | [8 empty] | 0.5
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [63 empty] | 1 | [8 empty] | 0.54
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.1 | [6 empty] | 0.21
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.2 | [6 empty] | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.3 | [6 empty] | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.4 | [6 empty] | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.5 | [6 empty] | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.6 | [6 empty] | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.7 | [6 empty] | 0.22
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.8 | [6 empty] | 0.25
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 0.9 | [6 empty] | 0.35
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [65 empty] | 1 | [6 empty] | 0.53
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall |  | t (in) | L (in) | D (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [13 empty] | 0 |  |  | 0 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall |  | t (mm) | L (mm) | D (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | screen | [20 empty] | 0.02 |  |  | 0 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [13 empty] | perforated plate | [20 empty] | 0.05 |  |  | 0 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.002 | [35 empty] | 0.57
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.002 | [35 empty] | 0.51
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.002 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.01 | [35 empty] | 0.68
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.01 | [35 empty] | 0.52
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.01 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.05 | [35 empty] | 0.8
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.05 | [35 empty] | 0.55
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.05 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.2 | [35 empty] | 0.92
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.2 | [35 empty] | 0.66
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.2 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.5 | [35 empty] | 1
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.5 | [35 empty] | 0.72
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.5 | [35 empty] | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0 |  |  | 1 | [35 empty] | 1
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 1 | [35 empty] | 0.72
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 1 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall |  | t (in) | L (in) | H (in) | W (in) | Q (cfm) | obstruction - select from list | N/A | N/A | [5 empty] | none (open) |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [13 empty] | 0 |  |  | 0 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall |  | t (mm) | L (mm) | H (mm) | W (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | [5 empty] | screen | [19 empty] | 0.02 |  |  | 0 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [14 empty] | perforated plate | [19 empty] | 0.05 |  |  | 0 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.002 | [35 empty] | 0.57
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.002 | [35 empty] | 0.51
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.002 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.01 | [35 empty] | 0.68
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.01 | [35 empty] | 0.52
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.01 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.05 | [35 empty] | 0.8
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.05 | [35 empty] | 0.55
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.05 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.2 | [35 empty] | 0.92
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.2 | [35 empty] | 0.66
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.2 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 0.5 | [35 empty] | 1
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 0.5 | [35 empty] | 0.72
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 0.5 | [35 empty] | 0.5
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0 |  |  | 1 | [35 empty] | 1
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.02 |  |  | 1 | [35 empty] | 0.72
A12A2 | A-12 | Entries | A | Rectangular | Rectangular Duct Mounted in Wall | [34 empty] | 0.05 |  |  | 1 | [35 empty] | 0.5
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall |  | R (in) | D (in) | Dₛ (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  | none (open) |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [17 empty] | 0 | [34 empty] | 1
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall |  | R (mm) | D (mm) | Dₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  | screen | [25 empty] | 0.01 | [34 empty] | 0.87
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.02 | [34 empty] | 0.74
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.03 | [34 empty] | 0.61
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.04 | [34 empty] | 0.51
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.05 | [34 empty] | 0.4
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.06 | [34 empty] | 0.32
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.08 | [34 empty] | 0.2
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.1 | [34 empty] | 0.15
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.12 | [34 empty] | 0.1
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.16 | [34 empty] | 0.06
A12B | A-12 | Entries | B | Round | Smooth Covering Bellmouth, without End Wall | [38 empty] | 0.2 | [34 empty] | 0.03
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall |  | R (in) | D (in) | Dₛ (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  | none (open) |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [17 empty] | 0 | [34 empty] | 0.5
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall |  | R (mm) | D (mm) | Dₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  | screen | [25 empty] | 0.01 | [34 empty] | 0.43
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.02 | [34 empty] | 0.36
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.03 | [34 empty] | 0.31
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.04 | [34 empty] | 0.26
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.05 | [34 empty] | 0.22
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.06 | [34 empty] | 0.2
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.08 | [34 empty] | 0.15
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.1 | [34 empty] | 0.12
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.12 | [34 empty] | 0.09
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.16 | [34 empty] | 0.06
A12C | A-12 | Entries | C | Round | Smooth Covering Bellmouth, with End Wall | [38 empty] | 0.2 | [34 empty] | 0.03
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall |  | L (in) | D (in) | Dₛ (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.025 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall |  | L (mm) | D (mm) | Dₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | screen | [23 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 0 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 10 |  |  | 0.47
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.42
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 10 |  |  | 0.39
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.37
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 10 |  |  | 0.27
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 20 |  |  | 0.45
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.35
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 20 |  |  | 0.32
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.27
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 20 |  |  | 0.18
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 30 |  |  | 0.43
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.3
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 30 |  |  | 0.25
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.2
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 30 |  |  | 0.13
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 40 |  |  | 0.41
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.26
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 40 |  |  | 0.22
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.16
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 40 |  |  | 0.11
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 60 |  |  | 0.4
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.23
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 60 |  |  | 0.18
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.15
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 60 |  |  | 0.12
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 100 |  |  | 0.42
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.3
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 100 |  |  | 0.27
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.25
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 100 |  |  | 0.23
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.4
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 140 |  |  | 0.38
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.37
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 140 |  |  | 0.36
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 180 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A12D1 | A-12 | Entries | D | Round | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall |  | L (in) | H (in) | W (in) | Hₛ (in) | Wₛ (in) | Q (cfm) | obstruction - select from list | N/A | [6 empty] | none (open) |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.025 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall |  | L (mm) | H (mm) | W (mm) | Hₛ (mm) | Wₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | [6 empty] | screen | [21 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 0 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 10 |  |  | 0.47
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.42
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 10 |  |  | 0.39
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.37
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 10 |  |  | 0.27
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 20 |  |  | 0.45
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.35
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 20 |  |  | 0.32
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.27
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 20 |  |  | 0.18
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 30 |  |  | 0.43
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.3
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 30 |  |  | 0.25
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.2
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 30 |  |  | 0.13
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 40 |  |  | 0.41
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.26
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 40 |  |  | 0.22
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.16
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 40 |  |  | 0.11
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 60 |  |  | 0.4
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.23
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 60 |  |  | 0.18
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.15
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 60 |  |  | 0.12
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 100 |  |  | 0.42
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.3
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 100 |  |  | 0.27
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.25
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 100 |  |  | 0.23
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.4
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 140 |  |  | 0.38
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.37
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 140 |  |  | 0.36
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.25 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A12D2 | A-12 | Entries | D | Rectangular | Conical Converging Bellmouth, without End Wall | [37 empty] | 1 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall |  | L (in) | D (in) | Dₛ (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.025 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall |  | L (mm) | D (mm) | Dₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | screen | [23 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 10 |  |  | 0.47
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 10 |  |  | 0.42
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.39
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 10 |  |  | 0.37
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.27
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 20 |  |  | 0.45
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 20 |  |  | 0.35
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.32
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 20 |  |  | 0.27
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.18
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 30 |  |  | 0.43
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 30 |  |  | 0.3
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.25
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 30 |  |  | 0.2
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.13
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 40 |  |  | 0.41
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 40 |  |  | 0.26
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.22
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 40 |  |  | 0.16
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.11
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 60 |  |  | 0.4
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 60 |  |  | 0.23
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.18
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 60 |  |  | 0.15
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.12
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 100 |  |  | 0.42
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 100 |  |  | 0.3
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.27
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 100 |  |  | 0.25
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.23
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 140 |  |  | 0.4
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.38
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 140 |  |  | 0.37
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.36
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 180 |  |  | 0.5
A12E1 | A-12 | Entries | E | Round | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall |  | L (in) | H (in) | W (in) | Hₛ (in) | Wₛ (in) | Q (cfm) | obstruction - select from list | N/A | [6 empty] | none (open) |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.025 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall |  | L (mm) | H (mm) | W (mm) | Hₛ (mm) | Wₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | [6 empty] | screen | [21 empty] | 0.05 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 10 |  |  | 0.47
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 10 |  |  | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 10 |  |  | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 10 |  |  | 0.39
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 10 |  |  | 0.37
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 10 |  |  | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 20 |  |  | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 20 |  |  | 0.41
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 20 |  |  | 0.35
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 20 |  |  | 0.32
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 20 |  |  | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 20 |  |  | 0.18
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 30 |  |  | 0.43
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 30 |  |  | 0.36
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 30 |  |  | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 30 |  |  | 0.25
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 30 |  |  | 0.2
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 30 |  |  | 0.13
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 40 |  |  | 0.41
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 40 |  |  | 0.33
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 40 |  |  | 0.26
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 40 |  |  | 0.22
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 40 |  |  | 0.16
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 40 |  |  | 0.11
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 60 |  |  | 0.4
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 60 |  |  | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 60 |  |  | 0.23
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 60 |  |  | 0.18
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 60 |  |  | 0.15
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 60 |  |  | 0.12
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 100 |  |  | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 100 |  |  | 0.35
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 100 |  |  | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 100 |  |  | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 100 |  |  | 0.25
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 100 |  |  | 0.23
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 140 |  |  | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 140 |  |  | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 140 |  |  | 0.4
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 140 |  |  | 0.38
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 140 |  |  | 0.37
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 140 |  |  | 0.36
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.025 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.05 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.075 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.1 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.15 | [32 empty] | 180 |  |  | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [37 empty] | 0.6 | [32 empty] | 180 |  |  | 0.5
A12F | A-12 | Entries | F | Round | Intake Hood |  | L (in) | D (in) | Dₛ (in) | θ (degrees) - select from list | Q (cfm) | obstruction - select from list | N/A | N/A |  |  |  | 0 |  | none (open) |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [16 empty] | 0.1 | [32 empty] | 0 |  |  | 2.6
A12F | A-12 | Entries | F | Round | Intake Hood |  | L (mm) | D (mm) | Dₛ (mm) | θ (degrees) | Q (m^3/hr) | obstruction - select from list | N/A | N/A |  |  |  | 15 |  | screen | [22 empty] | 0.1 | [32 empty] | 15 |  |  | 1.3
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.2 | [32 empty] | 0 |  |  | 1.8
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.2 | [32 empty] | 15 |  |  | 0.77
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.3 | [32 empty] | 0 |  |  | 1.5
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.3 | [32 empty] | 15 |  |  | 0.6
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.4 | [32 empty] | 0 |  |  | 1.4
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.4 | [32 empty] | 15 |  |  | 0.48
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.5 | [32 empty] | 0 |  |  | 1.3
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.5 | [32 empty] | 15 |  |  | 0.41
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 1.2
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.6 | [32 empty] | 15 |  |  | 0.3
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.7 | [32 empty] | 0 |  |  | 1.2
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.7 | [32 empty] | 15 |  |  | 0.29
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.8 | [32 empty] | 0 |  |  | 1.1
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.8 | [32 empty] | 15 |  |  | 0.28
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.9 | [32 empty] | 0 |  |  | 1.1
A12F | A-12 | Entries | F | Round | Intake Hood | [37 empty] | 0.9 | [32 empty] | 15 |  |  | 0.25
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged |  | hood profile - select from list | obstruction - select from list | #REF! | #REF! | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [10 empty] | round hood | [38 empty] | 0 |  |  | 1
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged |  | hood profile - select from list | obstruction - select from list |  | #REF! | N/A | N/A | N/A | N/A | [22 empty] | round hood | [38 empty] | 20 |  |  | 0.11
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 40 |  |  | 0.06
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 60 |  |  | 0.09
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 80 |  |  | 0.14
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 100 |  |  | 0.18
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 120 |  |  | 0.27
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 140 |  |  | 0.32
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 160 |  |  | 0.43
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | round hood | [38 empty] | 180 |  |  | 0.5
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [17 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [10 empty] | rect hood | [38 empty] | 0 |  |  | 1
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 20 |  |  | 0.19
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 40 |  |  | 0.13
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 60 |  |  | 0.16
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 80 |  |  | 0.21
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 100 |  |  | 0.27
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 120 |  |  | 0.33
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 140 |  |  | 0.43
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 160 |  |  | 0.53
A12G | A-12 | Entries | G | Round | Hood, Tapered, Flanged or Unflanged | [31 empty] | rect hood | [38 empty] | 180 |  |  | 0.62
A13A | A-13 | Exits | A | Round | Exhaust Hood |  | L (in) | D (in) | Dₛ (in) | θ (degrees) - select from list | Q (cfm) | obstruction - select from list | N/A | N/A |  |  |  | 0 |  | none (open) |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | 0.1 | [32 empty] | 0 |  |  | 4
A13A | A-13 | Exits | A | Round | Exhaust Hood |  | L (mm) | D (mm) | Dₛ (mm) | θ (degrees) | Q (m^3/hr) | obstruction - select from list | N/A | N/A |  |  |  | 15 |  | screen | [22 empty] | 0.1 | [32 empty] | 15 |  |  | 2.6
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.2 | [32 empty] | 0 |  |  | 2.3
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.2 | [32 empty] | 15 |  |  | 1.2
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.25 | [32 empty] | 0 |  |  | 1.9
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.25 | [32 empty] | 15 |  |  | 1
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.3 | [32 empty] | 0 |  |  | 1.6
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.3 | [32 empty] | 15 |  |  | 0.8
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.35 | [32 empty] | 0 |  |  | 1.4
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.35 | [32 empty] | 15 |  |  | 0.7
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.4 | [32 empty] | 0 |  |  | 1.3
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.4 | [32 empty] | 15 |  |  | 0.65
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.5 | [32 empty] | 0 |  |  | 1.2
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.5 | [32 empty] | 15 |  |  | 0.6
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.6 | [32 empty] | 0 |  |  | 1.1
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.6 | [32 empty] | 15 |  |  | 0.6
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.8 | [32 empty] | 0 |  |  | 1.1
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 0.8 | [32 empty] | 15 |  |  | 0.6
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 1 | [32 empty] | 0 |  |  | 1
A13A | A-13 | Exits | A | Round | Exhaust Hood | [37 empty] | 1 | [32 empty] | 15 |  |  | 0.6
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall |  | L (in) | D (in) | Dₛ (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [23 empty] | 2 | [19 empty] | 14 |  |  | 0.33
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall |  | L (mm) | D (mm) | Dₛ (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A |  |  |  |  | screen | [36 empty] | 4 | [19 empty] | 14 |  |  | 0.24
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 14 |  |  | 0.22
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 14 |  |  | 0.19
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 14 |  |  | 0.17
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 16 |  |  | 0.36
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 16 |  |  | 0.28
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 16 |  |  | 0.25
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 16 |  |  | 0.23
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 16 |  |  | 0.2
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 20 |  |  | 0.44
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 20 |  |  | 0.36
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 20 |  |  | 0.32
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 20 |  |  | 0.3
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 20 |  |  | 0.27
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 30 |  |  | 0.74
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 30 |  |  | 0.54
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 30 |  |  | 0.49
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 30 |  |  | 0.5
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 30 |  |  | 0.49
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 45 |  |  | 0.97
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 45 |  |  | 0.94
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 45 |  |  | 0.94
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 45 |  |  | 0.94
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 45 |  |  | 0.94
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 60 |  |  | 0.99
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 60 |  |  | 0.1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 60 |  |  | 0.98
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 60 |  |  | 0.72
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 60 |  |  | 1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 2 | [19 empty] | 90 |  |  | 1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 4 | [19 empty] | 90 |  |  | 1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 6 | [19 empty] | 90 |  |  | 1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 10 | [19 empty] | 90 |  |  | 1
A13B | A-13 | Exits | B | Round | Conical, With or without a Wall | [50 empty] | 16 | [19 empty] | 90 |  |  | 1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall |  | H (in) | Hₛ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | obstruction - select from list | #REF! | N/A | [5 empty] | none (open) |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [23 empty] | 2 | [19 empty] | 14 |  |  | 0.37
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall |  | H (mm) | Hₛ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | obstruction - select from list | #REF! | N/A | [5 empty] | screen | [35 empty] | 4 | [19 empty] | 14 |  |  | 0.25
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 14 |  |  | 0.28
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 20 |  |  | 0.38
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 20 |  |  | 0.37
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 20 |  |  | 0.47
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 30 |  |  | 0.5
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 30 |  |  | 0.57
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 30 |  |  | 0.64
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 45 |  |  | 0.75
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 45 |  |  | 0.82
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 45 |  |  | 0.87
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 60 |  |  | 0.9
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 60 |  |  | 1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 60 |  |  | 1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 90 |  |  | 1.1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 90 |  |  | 1.1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 90 |  |  | 1.1
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall |  | H (in) | W (in) | Hₛ (in) | Wₛ (in) | L (in) | Q (cfm) | obstruction - select from list | #REF! | [6 empty] | none (open) |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [23 empty] | 2 | [19 empty] | 10 |  |  | 0.44
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall |  | H (mm) | W (mm) | Hₛ (mm) | Wₛ (mm) | L (mm) | Q (m^3/hr) | obstruction - select from list | #REF! | [6 empty] | screen | [34 empty] | 4 | [19 empty] | 10 |  |  | 0.31
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 10 |  |  | 0.29
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 10 |  |  | 0.26
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 14 |  |  | 0.58
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 14 |  |  | 0.48
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 14 |  |  | 0.47
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 14 |  |  | 0.45
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 20 |  |  | 0.7
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 20 |  |  | 0.61
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 20 |  |  | 0.62
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 20 |  |  | 0.6
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 30 |  |  | 0.86
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 30 |  |  | 0.76
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 30 |  |  | 0.74
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 30 |  |  | 0.73
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 45 |  |  | 1
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 45 |  |  | 0.94
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 45 |  |  | 0.94
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 45 |  |  | 0.89
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 2 | [19 empty] | 60 |  |  | 1.1
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 4 | [19 empty] | 60 |  |  | 1.1
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 6 | [19 empty] | 60 |  |  | 1.1
A13D | A-13 | Exits | D | Rectangular | Pyramidal Diffuser, With or without a Wall | [50 empty] | 10 | [19 empty] | 60 |  |  | 1
A13E1 | A-13 | Exits | E | Round | Discharge to Atmosphere from a 90° elbow |  | D (in) | L (in) | Q (cfm) | obstruction - select from list | N/A | N/A | N/A | N/A | 0.9 |  | none (open) | [5 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | 0.9 | [35 empty] | 1.5
A13E1 | A-13 | Exits | E | Round | Discharge to Atmosphere from a 90° elbow |  | D (mm) | L (mm) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | N/A | N/A | 1.3 |  | screen | [25 empty] | 1.3 | [35 empty] | 1.4
A13E1 | A-13 | Exits | E | Round | Discharge to Atmosphere from a 90° elbow
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow |  | H (in) | W (in) | L (in) | R (in) | Q (cfm) | obstruction - select from list | #REF! | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [14 empty] | 0 | 0 | [30 empty] | 3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow |  | H (mm) | W (mm) | L (mm) | R (mm) | Q (m^3/hr) | obstruction - select from list | #REF! | N/A |  |  |  |  | screen | [27 empty] | 0 | 0.75 | [30 empty] | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0 | 1 | [30 empty] | 1.8
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0 | 1.5 | [30 empty] | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0 | 2.5 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0.5 | 0 | [30 empty] | 3.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0.5 | 0.75 | [30 empty] | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0.5 | 1 | [30 empty] | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0.5 | 1.5 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 0.5 | 2.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1 | 0 | [30 empty] | 3.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1 | 0.75 | [30 empty] | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1 | 1 | [30 empty] | 1.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1 | 2.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1.5 | 0 | [30 empty] | 3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1.5 | 0.75 | [30 empty] | 1.8
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1.5 | 1 | [30 empty] | 1.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1.5 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 1.5 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 2 | 0 | [30 empty] | 2.7
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 2 | 0.75 | [30 empty] | 1.7
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 2 | 1 | [30 empty] | 1.3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 2 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 2 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 3 | 0 | [30 empty] | 2.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 3 | 0.75 | [30 empty] | 1.6
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 3 | 1 | [30 empty] | 1.3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 3 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 3 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 4 | 0 | [30 empty] | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 4 | 0.75 | [30 empty] | 1.6
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 4 | 1 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 4 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 4 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 6 | 0 | [30 empty] | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 6 | 0.75 | [30 empty] | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 6 | 1 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 6 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 6 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 8 | 0 | [30 empty] | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 8 | 0.75 | [30 empty] | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 8 | 1 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 8 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 8 | 2.5 | [30 empty] | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 12 | 0 | [30 empty] | 2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 12 | 0.75 | [30 empty] | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 12 | 1 | [30 empty] | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 12 | 1.5 | [30 empty] | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [41 empty] | 12 | 2.5 | [30 empty] | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall |  | H (in) | W (in) | θ (degrees) | V (fps) | Q_0 (cfm) | obstruction - select from list | #REF! | N/A | [5 empty] | none (open) |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [16 empty] | 0.1-0.2 | [17 empty] | 0 | [8 empty] | 90 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall |  | H (mm) | W (mm) | θ (degrees) | V (m/s) | Q_0 (m^3/hr) | obstruction - select from list | #REF! | N/A | [5 empty] | screen | [28 empty] | 0.1-0.2 | [17 empty] | 0 | [8 empty] | 120 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 0 | [8 empty] | 150 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 0.5 | [8 empty] | 90 |  |  | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 0.5 | [8 empty] | 120 |  |  | 0.92
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 0.5 | [8 empty] | 150 |  |  | 0.75
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1 | [8 empty] | 90 |  |  | 1.2
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1 | [8 empty] | 120 |  |  | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1 | [8 empty] | 150 |  |  | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1.5 | [8 empty] | 90 |  |  | 1.5
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1.5 | [8 empty] | 120 |  |  | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 1.5 | [8 empty] | 150 |  |  | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 2 | [8 empty] | 90 |  |  | 1.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 2 | [8 empty] | 120 |  |  | 1.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.1-0.2 | [17 empty] | 2 | [8 empty] | 150 |  |  | 1.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0 | [8 empty] | 45 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0 | [8 empty] | 60 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0 | [8 empty] | 90 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0 | [8 empty] | 120 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0 | [8 empty] | 150 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0.5 | [8 empty] | 45 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0.5 | [8 empty] | 60 |  |  | 0.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0.5 | [8 empty] | 90 |  |  | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0.5 | [8 empty] | 120 |  |  | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 0.5 | [8 empty] | 150 |  |  | 0.82
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1 | [8 empty] | 45 |  |  | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1 | [8 empty] | 60 |  |  | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1 | [8 empty] | 90 |  |  | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1 | [8 empty] | 120 |  |  | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1 | [8 empty] | 150 |  |  | 0.83
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1.5 | [8 empty] | 45 |  |  | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1.5 | [8 empty] | 60 |  |  | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1.5 | [8 empty] | 90 |  |  | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1.5 | [8 empty] | 120 |  |  | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 1.5 | [8 empty] | 150 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 2 | [8 empty] | 45 |  |  | 1.6
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 2 | [8 empty] | 60 |  |  | 1.6
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 2 | [8 empty] | 90 |  |  | 1.7
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 2 | [8 empty] | 120 |  |  | 1.7
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 0.5-2.0 | [17 empty] | 2 | [8 empty] | 150 |  |  | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0 | [8 empty] | 45 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0 | [8 empty] | 60 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0 | [8 empty] | 90 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0 | [8 empty] | 120 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0.5 | [8 empty] | 45 |  |  | 0.92
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0.5 | [8 empty] | 60 |  |  | 0.87
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0.5 | [8 empty] | 90 |  |  | 0.82
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 0.5 | [8 empty] | 120 |  |  | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1 | [8 empty] | 45 |  |  | 0.93
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1 | [8 empty] | 60 |  |  | 0.87
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1 | [8 empty] | 90 |  |  | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1 | [8 empty] | 120 |  |  | 0.76
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1.5 | [8 empty] | 45 |  |  | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1.5 | [8 empty] | 60 |  |  | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1.5 | [8 empty] | 90 |  |  | 0.97
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 1.5 | [8 empty] | 120 |  |  | 0.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 2 | [8 empty] | 45 |  |  | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 2 | [8 empty] | 60 |  |  | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 2 | [8 empty] | 90 |  |  | 1.2
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [43 empty] | 5--10 | [17 empty] | 2 | [8 empty] | 120 |  |  | 0.98
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall |  | D (in) | θ (degrees) | V (fpm) | Q_0 (cfm) | obstruction - select from type | #REF! | N/A | N/A |  |  |  |  | none (open) |  |  |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [34 empty] | 0 | [8 empty] | 45 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall |  | D (mm) | θ (degrees) | V (m/s) | Q_0 (m^3/hr) | obstruction - select from type | #REF! | N/A | N/A |  |  |  |  | screen | [47 empty] | 0 | [8 empty] | 60 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0 | [8 empty] | 90 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0 | [8 empty] | 120 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0 | [8 empty] | 150 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0.5 | [8 empty] | 45 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0.5 | [8 empty] | 60 |  |  | 0.9
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0.5 | [8 empty] | 90 |  |  | 0.8
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0.5 | [8 empty] | 120 |  |  | 0.8
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 0.5 | [8 empty] | 150 |  |  | 0.82
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1 | [8 empty] | 45 |  |  | 1.1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1 | [8 empty] | 60 |  |  | 1.1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1 | [8 empty] | 90 |  |  | 0.95
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1 | [8 empty] | 120 |  |  | 0.95
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1 | [8 empty] | 150 |  |  | 0.83
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1.5 | [8 empty] | 45 |  |  | 1.3
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1.5 | [8 empty] | 60 |  |  | 1.4
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1.5 | [8 empty] | 90 |  |  | 1.4
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1.5 | [8 empty] | 120 |  |  | 1.3
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 1.5 | [8 empty] | 150 |  |  | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 2 | [8 empty] | 45 |  |  | 1.6
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 2 | [8 empty] | 60 |  |  | 1.6
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 2 | [8 empty] | 90 |  |  | 1.7
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 2 | [8 empty] | 120 |  |  | 1.7
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [61 empty] | 2 | [8 empty] | 150 |  |  | 1.3
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork |  | H (in) | W (in) | H₁ (in) | angle (deg) | Q (cfm) | obstruction - select from list | N/A | N/A | [6 empty] | none (open) |  | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.51
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork |  | H (mm) | W (mm) | H₁ (mm) | angle (deg) | Q (m^3/hr) | obstruction - select from list | N/A | N/A | [6 empty] | screen | [33 empty] | 1.5 | [20 empty] | 15 |  |  | 0.54
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 1.5 | [20 empty] | 20 |  |  | 0.55
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 1.5 | [20 empty] | 25 |  |  | 0.59
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 1.5 | [20 empty] | 30 |  |  | 0.63
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 1.5 | [20 empty] | 35 |  |  | 0.65
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.34
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.36
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.38
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.43
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.5
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2 | [20 empty] | 35 |  |  | 0.56
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.25
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.27
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.31
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.37
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.46
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 2.5 | [20 empty] | 35 |  |  | 0.53
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.21
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.24
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.27
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.35
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.44
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3 | [20 empty] | 35 |  |  | 0.52
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.18
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.22
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.25
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.33
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.43
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 3.5 | [20 empty] | 35 |  |  | 0.51
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.17
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.2
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.24
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.33
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.42
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [49 empty] | 4 | [20 empty] | 35 |  |  | 0.5
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser |  | H (in) | W (in) | H₁ (in) | W₁ (in) | L (in) | Q (cfm) | obstruction - select from list | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [22 empty] | 1.5 | [20 empty] | 10 |  |  | 0.54
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser |  | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | L (mm) | Q (m^3/hr) | obstruction - select from list | N/A | [40 empty] | 1.5 | [20 empty] | 15 |  |  | 0.67
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 1.5 | [20 empty] | 20 |  |  | 0.45
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 1.5 | [20 empty] | 25 |  |  | 0.8
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 1.5 | [20 empty] | 30 |  |  | 0.85
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2 | [20 empty] | 10 |  |  | 0.42
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2 | [20 empty] | 15 |  |  | 0.58
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2 | [20 empty] | 20 |  |  | 0.67
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2 | [20 empty] | 25 |  |  | 0.74
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2 | [20 empty] | 30 |  |  | 0.78
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2.5 | [20 empty] | 10 |  |  | 0.37
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2.5 | [20 empty] | 15 |  |  | 0.53
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2.5 | [20 empty] | 20 |  |  | 0.65
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2.5 | [20 empty] | 25 |  |  | 0.72
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 2.5 | [20 empty] | 30 |  |  | 0.76
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3 | [20 empty] | 10 |  |  | 0.34
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3 | [20 empty] | 15 |  |  | 0.51
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3 | [20 empty] | 20 |  |  | 0.64
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3 | [20 empty] | 25 |  |  | 0.7
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3 | [20 empty] | 30 |  |  | 0.75
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3.5 | [20 empty] | 10 |  |  | 0.32
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3.5 | [20 empty] | 15 |  |  | 0.5
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3.5 | [20 empty] | 20 |  |  | 0.64
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3.5 | [20 empty] | 25 |  |  | 0.7
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 3.5 | [20 empty] | 30 |  |  | 0.75
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 4 | [20 empty] | 10 |  |  | 0.31
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 4 | [20 empty] | 15 |  |  | 0.51
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 4 | [20 empty] | 20 |  |  | 0.65
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 4 | [20 empty] | 25 |  |  | 0.72
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [49 empty] | 4 | [20 empty] | 30 |  |  | 0.76
A13I | A-13 | Exits | I | Rectangular | Fan, Free Discharge, Plenum |  | input 1: Fan Type - select from list | Airfoil wheels - backwardly inclined | [7 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | Airfoil wheels - backwardly inclined | [41 empty] | 1
A13I | A-13 | Exits | I | Rectangular | Fan, Free Discharge, Plenum |  | input 1: Fan Type - select from list | Backwardly inclined wheels | [21 empty] | Backwardly inclined wheels | [41 empty] | 1.5
A13I | A-13 | Exits | I | Rectangular | Fan, Free Discharge, Plenum | [9 empty] | Forward curved wheel | [21 empty] | Forward curved wheel | [41 empty] | 1.8
A13J1 | A-13 | Exits | J | Round | Abrupt, with or without Wall | [17 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A
A13J1 | A-13 | Exits | J | Round | Abrupt, with or without Wall
A13J2 | A-13 | Exits | J | Rectangular | Abrupt, with or without Wall | [17 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A
A13J2 | A-13 | Exits | J | Rectangular | Abrupt, with or without Wall
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct |  | D (in) | Q (cfm) | n, free area ratio | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  | 0.3 | [44 empty] | 6.2
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct |  | D (mm) | Q (m^3/hr) | n, free area ratio | N/A | N/A | N/A | N/A | N/A | [19 empty] | 0.4 | [44 empty] | 3
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.5 | [44 empty] | 1.7
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.55 | [44 empty] | 1.3
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.6 | [44 empty] | 0.97
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.65 | [44 empty] | 0.75
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.7 | [44 empty] | 0.58
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.75 | [44 empty] | 0.44
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.8 | [44 empty] | 0.32
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 0.9 | [44 empty] | 0.14
A14A1 | A-14 | Screens & Plates | A | Round | Screen in Duct | [28 empty] | 1 | [44 empty] | 0
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct |  | H (in) | W (in) | Q (cfm) | n, free area ratio | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  | 0.3 | [44 empty] | 6.2
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct |  | H (mm) | W (mm) | Q (m^3/hr) | n, free area ratio | N/A | N/A | N/A | N/A | [19 empty] | 0.4 | [44 empty] | 3
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.5 | [44 empty] | 1.7
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.55 | [44 empty] | 1.3
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.6 | [44 empty] | 0.97
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.65 | [44 empty] | 0.75
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.7 | [44 empty] | 0.58
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.75 | [44 empty] | 0.44
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.8 | [44 empty] | 0.32
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 0.9 | [44 empty] | 0.14
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [28 empty] | 1 | [44 empty] | 0
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick |  | D (in) | Q (cfm) | n, free area ratio | plate thickness (in) | perforated hole diameter (in) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  | 0.2 | [5 empty] | 0.015 | [38 empty] | 52
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick |  | D (mm) | Q (m^3/hr) | n, free area ratio | plate thickness (mm) | perforated hole diameter (mm) | N/A | N/A | N/A | [19 empty] | 0.2 | [5 empty] | 0.2 | [38 empty] | 48
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.2 | [5 empty] | 0.4 | [38 empty] | 46
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.2 | [5 empty] | 0.6 | [38 empty] | 42
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.015 | [38 empty] | 30
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.2 | [38 empty] | 28
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.4 | [38 empty] | 27
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.6 | [38 empty] | 24
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.015 | [38 empty] | 18
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.2 | [38 empty] | 17
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.4 | [38 empty] | 17
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.6 | [38 empty] | 15
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.015 | [38 empty] | 8.2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.2 | [38 empty] | 7.7
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.4 | [38 empty] | 7.4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.6 | [38 empty] | 6.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.015 | [38 empty] | 4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.2 | [38 empty] | 3.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.4 | [38 empty] | 3.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.6 | [38 empty] | 3.2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.015 | [38 empty] | 2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.2 | [38 empty] | 1.9
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.4 | [38 empty] | 1.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.6 | [38 empty] | 1.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.015 | [38 empty] | 0.97
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.2 | [38 empty] | 0.91
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.4 | [38 empty] | 0.88
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.6 | [38 empty] | 0.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.015 | [38 empty] | 0.42
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.2 | [38 empty] | 0.4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.4 | [38 empty] | 0.39
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.6 | [38 empty] | 0.36
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.015 | [38 empty] | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.2 | [38 empty] | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.4 | [38 empty] | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.6 | [38 empty] | 0.13
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick |  | H (in) | W (in) | Q (cfm) | n, free area ratio | plate thickness (in) | perforated hole diameter (in) | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A |  | 0.2 | [5 empty] | 0.015 | [38 empty] | 52
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick |  | H (mm) | W (mm) | Q (m^3/hr) | n, free area ratio | plate thickness (mm) | perforated hole diameter (mm) | N/A | N/A | [19 empty] | 0.2 | [5 empty] | 0.2 | [38 empty] | 48
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.2 | [5 empty] | 0.4 | [38 empty] | 46
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.2 | [5 empty] | 0.6 | [38 empty] | 42
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.015 | [38 empty] | 30
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.2 | [38 empty] | 28
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.4 | [38 empty] | 27
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.25 | [5 empty] | 0.6 | [38 empty] | 24
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.015 | [38 empty] | 18
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.2 | [38 empty] | 17
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.4 | [38 empty] | 17
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.3 | [5 empty] | 0.6 | [38 empty] | 15
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.015 | [38 empty] | 8.2
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.2 | [38 empty] | 7.7
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.4 | [38 empty] | 7.4
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.4 | [5 empty] | 0.6 | [38 empty] | 6.6
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.015 | [38 empty] | 4
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.2 | [38 empty] | 3.8
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.4 | [38 empty] | 3.6
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.5 | [5 empty] | 0.6 | [38 empty] | 3.2
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.015 | [38 empty] | 2
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.2 | [38 empty] | 1.9
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.4 | [38 empty] | 1.8
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.6 | [5 empty] | 0.6 | [38 empty] | 1.6
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.015 | [38 empty] | 0.97
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.2 | [38 empty] | 0.91
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.4 | [38 empty] | 0.88
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.7 | [5 empty] | 0.6 | [38 empty] | 0.8
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.015 | [38 empty] | 0.42
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.2 | [38 empty] | 0.4
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.4 | [38 empty] | 0.39
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.8 | [5 empty] | 0.6 | [38 empty] | 0.36
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.015 | [20 empty] | 0.3 | [17 empty] | 0.13
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.2 | [20 empty] | 0.4 | [17 empty] | 0.13
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.4 | [20 empty] | 0.5 | [17 empty] | 0.13
A14B2 | A-14 | Screens & Plates | B | Rectangular | Perforated Plate in Duct, Thick | [28 empty] | 0.9 | [5 empty] | 0.6 | [20 empty] | 0.6 | [17 empty] | 0.13
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate |  | D (in) | Q (cfm) | θ (degrees) | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [28 empty] | 0.8 | [14 empty] | 0 |  |  | 0.2
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate |  | D (mm) | Q (m^3/hr) | θ (degrees) | N/A | N/A | N/A | N/A | N/A | [46 empty] | 1 | [14 empty] | 10 |  |  | 0.52
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate | [55 empty] | 1.5 | [14 empty] | 20 |  |  | 1.5
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate | [55 empty] | 0.3 | [14 empty] | 30 |  |  | 4.5
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate | [55 empty] | 0.4 | [14 empty] | 40 |  |  | 11
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate | [55 empty] | 0.5 | [14 empty] | 50 |  |  | 29
A15A | A-15 | Obstructions | A | Round | Damper, Butterfly, Thin Plate | [55 empty] | 0.6 | [14 empty] | 60 |  |  | 108
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate |  | H (in) | W (in) | Q (cfm) | θ (degrees) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [28 empty] | 0.8 | [14 empty] | 0 |  |  | 0.04
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate |  | H (mm) | W (mm) | Q (m^3/hr) | θ (degrees) | N/A | N/A | N/A | N/A | [46 empty] | 1 | [14 empty] | 10 |  |  | 0.33
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate | [55 empty] | 1.5 | [14 empty] | 20 |  |  | 1.2
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate | [55 empty] | 0.3 | [14 empty] | 30 |  |  | 3.3
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate | [55 empty] | 0.4 | [14 empty] | 40 |  |  | 9
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate | [55 empty] | 0.5 | [14 empty] | 50 |  |  | 26
A15B | A-15 | Obstructions | B | Rectangular | Damper, Butterfly, Thin Plate | [55 empty] | 0.6 | [14 empty] | 60 |  |  | 70
A15C | A-15 | Obstructions | C | Round | Damper, Gate |  | D (in) | h (in) | Q (cfm) | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [8 empty] | 0.2 | [15 empty] | 0.25 |  |  |  | 0.8 | [17 empty] | 35
A15C | A-15 | Obstructions | C | Round | Damper, Gate |  | D (mm) | h (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | N/A | [26 empty] | 0.3 | [15 empty] | 0.38 |  |  |  | 1 | [17 empty] | 10
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.4 | [15 empty] | 0.5 |  |  |  | 1.5 | [17 empty] | 4.6
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.5 | [15 empty] | 0.61 |  |  |  | 0.3 | [17 empty] | 2.1
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.6 | [15 empty] | 0.71 |  |  |  | 0.4 | [17 empty] | 0.98
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.7 | [15 empty] | 0.81 |  |  |  | 0.5 | [17 empty] | 0.44
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.8 | [15 empty] | 0.9 |  |  |  | 0.6 | [17 empty] | 0.17
A15C | A-15 | Obstructions | C | Round | Damper, Gate | [35 empty] | 0.9 | [15 empty] | 0.96 |  |  |  | 0.8 | [17 empty] | 0.06
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate |  | H (in) | W (in) | h (in) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [16 empty] | 0.5 |  |  | 0.3 | [8 empty] | 1 | [17 empty] | 14
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate |  | H (mm) | W (mm) | h (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [34 empty] | 1 |  |  | 0.3 | [8 empty] | 1.5 | [17 empty] | 19
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.3 | [8 empty] | 0.3 | [17 empty] | 20
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.3 | [8 empty] | 0.4 | [17 empty] | 18
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.4 | [8 empty] | 0.5 | [17 empty] | 6.9
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.4 | [8 empty] | 0.6 | [17 empty] | 8.8
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.4 | [8 empty] | 0.8 | [17 empty] | 9.1
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.4 | [8 empty] | 1 | [17 empty] | 8.8
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.5 | [8 empty] | 1.5 | [17 empty] | 3.3
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.5 | [8 empty] | 0.3 | [17 empty] | 4.5
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.5 | [8 empty] | 0.4 | [17 empty] | 4.7
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.5 | [8 empty] | 0.5 | [17 empty] | 4.5
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.6 | [8 empty] | 0.6 | [17 empty] | 1.7
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.6 | [8 empty] | 0.8 | [17 empty] | 2.4
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.6 | [8 empty] | 1 | [17 empty] | 2.7
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.6 | [8 empty] | 1.5 | [17 empty] | 2.3
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.7 | [8 empty] | 0.3 | [17 empty] | 0.83
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.7 | [8 empty] | 0.4 | [17 empty] | 1.2
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.7 | [8 empty] | 0.5 | [17 empty] | 1.2
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.7 | [8 empty] | 0.6 | [17 empty] | 1.1
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.8 | [8 empty] | 0.8 | [17 empty] | 0.32
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.8 | [8 empty] | 1 | [17 empty] | 0.55
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.8 | [8 empty] | 1.5 | [17 empty] | 0.47
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.8 | [8 empty] | 0.3 | [17 empty] | 0.51
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 0.5 |  |  | 0.9 | [8 empty] | 0.4 | [17 empty] | 0.09
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1 |  |  | 0.9 | [8 empty] | 0.5 | [17 empty] | 0.17
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 1.5 |  |  | 0.9 | [8 empty] | 0.6 | [17 empty] | 0.11
A15D | A-15 | Obstructions | D | Rectangular | Damper, Gate | [43 empty] | 2 |  |  | 0.9 | [8 empty] | 0.8 | [17 empty] | 0.13
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades |  | H (in) | W (in) | # blades - select from list | θ (degrees) | Q (cfm) | N/A | N/A | N/A |  |  | 1 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 80 |  |  | 116
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades |  | H (mm) | W (mm) | # blades - select from list | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A |  |  | 2 | [27 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 80 |  |  | 152
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [11 empty] | 3 | [27 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 80 |  |  | 188
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 80 |  |  | 245
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 80 |  |  | 284
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 80 |  |  | 361
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 80 |  |  | 576
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 70 |  |  | 32
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 70 |  |  | 38
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 70 |  |  | 45
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 70 |  |  | 45
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 70 |  |  | 55
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 70 |  |  | 65
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 70 |  |  | 102
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 60 |  |  | 14
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 60 |  |  | 16
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 60 |  |  | 18
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 60 |  |  | 21
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 60 |  |  | 22
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 60 |  |  | 24
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 60 |  |  | 28
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 50 |  |  | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 50 |  |  | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 50 |  |  | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 50 |  |  | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 50 |  |  | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 50 |  |  | 10
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 50 |  |  | 10
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 40 |  |  | 5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 40 |  |  | 6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 40 |  |  | 6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 40 |  |  | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 40 |  |  | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 40 |  |  | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 40 |  |  | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 30 |  |  | 2.3
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 30 |  |  | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 30 |  |  | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 30 |  |  | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 30 |  |  | 2.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 30 |  |  | 2.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 30 |  |  | 2.7
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 20 |  |  | 1.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 20 |  |  | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 20 |  |  | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 20 |  |  | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 20 |  |  | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 20 |  |  | 1.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 20 |  |  | 1.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 10 |  |  | 0.79
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 10 |  |  | 0.85
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 10 |  |  | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 10 |  |  | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 10 |  |  | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 10 |  |  | 1
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 10 |  |  | 1
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 0 |  |  | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades |  | H (in) | W (in) | # blades - select from list | θ (degrees) | Q (cfm) | N/A | N/A | N/A |  |  | 1 | [5 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 80 |  |  | 807
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades |  | H (mm) | W (mm) | # blades - select from list | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A |  |  | 2 | [27 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 80 |  |  | 915
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [11 empty] | 3 | [27 empty] | 0.5 | [15 empty] | 0.3 | [14 empty] | 80 |  |  | 1045
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [15 empty] | 0.4 | [14 empty] | 80 |  |  | 1121
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [15 empty] | 0.5 | [14 empty] | 80 |  |  | 1299
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [15 empty] | 0.6 | [14 empty] | 80 |  |  | 1521
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [15 empty] | 0.8 | [14 empty] | 80 |  |  | 1654
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [15 empty] | 1 | [14 empty] | 70 |  |  | 284
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [15 empty] | 1.5 | [14 empty] | 70 |  |  | 332
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 70 |  |  | 377
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 70 |  |  | 411
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 70 |  |  | 495
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 70 |  |  | 547
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 70 |  |  | 677
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 60 |  |  | 73
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 60 |  |  | 100
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 60 |  |  | 122
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 60 |  |  | 148
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 60 |  |  | 188
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 60 |  |  | 245
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 60 |  |  | 361
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 50 |  |  | 21
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 50 |  |  | 28
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 50 |  |  | 33
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 50 |  |  | 38
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 50 |  |  | 54
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 50 |  |  | 65
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 50 |  |  | 107
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 40 |  |  | 9
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 40 |  |  | 11
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 40 |  |  | 13
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 40 |  |  | 14
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 40 |  |  | 18
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 40 |  |  | 21
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 40 |  |  | 28
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 30 |  |  | 4.1
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 30 |  |  | 5
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 30 |  |  | 5.4
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 30 |  |  | 6
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 30 |  |  | 6.6
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 30 |  |  | 7.3
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 30 |  |  | 9
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 20 |  |  | 2.1
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 20 |  |  | 2.2
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 20 |  |  | 2.3
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 20 |  |  | 2.3
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 20 |  |  | 2.4
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 20 |  |  | 2.7
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 20 |  |  | 3.2
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 10 |  |  | 0.85
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 10 |  |  | 0.92
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 10 |  |  | 1
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 10 |  |  | 1
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 10 |  |  | 1.1
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 10 |  |  | 1.2
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 10 |  |  | 1.4
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.3 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.4 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.5 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.6 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 0.8 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1 | [30 empty] | 0 |  |  | 0.52
A15F | A-15 | Obstructions | F | Rectangular | Damper, Opposed Blades | [39 empty] | 1.5 | [30 empty] | 0 |  |  | 0.52
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade |  | H (in) | W (in) | θ (degrees) | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [43 empty] | 0 |  |  | 0.5
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade |  | H (mm) | W (mm) | θ (degrees) | Q (m^3/hr) | N/A | N/A | N/A | N/A | [61 empty] | 10 |  |  | 0.65
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade | [70 empty] | 20 |  |  | 1.6
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade | [70 empty] | 30 |  |  | 4
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade | [70 empty] | 40 |  |  | 9.4
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade | [70 empty] | 50 |  |  | 24
A15G | A-15 | Obstructions | G | Rectangular | Damper, Butterfly, Airfoil Blade | [70 empty] | 60 |  |  | 67
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct |  | D (in) | d (in) | L (in) | y (in) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | 0 | [10 empty] | 0.05 | [20 empty] | 0.1 |  |  |  | 1 | 3.9
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct |  | D (mm) | d (imm) | L (mm) | y (mm) | Q (m^3/hr) | N/A | N/A | N/A | [27 empty] | 0.05 | [10 empty] | 0.05 | [20 empty] | 0.5 |  |  |  | 0.97 | 1.5
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.1 | [10 empty] | 0.05 | [20 empty] | 1 |  |  |  | 0.93 | 0.66
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.15 | [10 empty] | 0.05 | [20 empty] | 5 |  |  |  | 0.89 | 0.3
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.2 | [10 empty] | 0.05 | [20 empty] | 10 |  |  |  | 0.84 | 0.17
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.25 | [10 empty] | 0.05 | [20 empty] | 50 |  |  |  | 0.79 | 0.11
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.3 | [10 empty] | 0.05 | [20 empty] | 100 |  |  |  | 0.74 | 0.1
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.35 | [10 empty] | 0.05 | [20 empty] | 500 |  |  |  | 0.67 | 0.07
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [36 empty] | 0.4 | [10 empty] | 0.05 | [20 empty] | 200000 |  |  |  | 0.58 | 0.07
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 300000 |  |  |  |  | 0.07
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 400000 |  |  |  |  | 0.05
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 500000 |  |  |  |  | 0.04
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 600000 |  |  |  |  | 0.02
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 1000000 |  |  |  |  | 0.02
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 0.1 |  |  |  |  | 8.4
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 0.5 |  |  |  |  | 3.2
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 1 |  |  |  |  | 1.4
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 5 |  |  |  |  | 0.64
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 10 |  |  |  |  | 0.38
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 50 |  |  |  |  | 0.24
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 100 |  |  |  |  | 0.21
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 500 |  |  |  |  | 0.15
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 200000 |  |  |  |  | 0.15
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 300000 |  |  |  |  | 0.16
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 400000 |  |  |  |  | 0.11
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 500000 |  |  |  |  | 0.09
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 600000 |  |  |  |  | 0.05
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 1000000 |  |  |  |  | 0.05
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 0.1 |  |  |  |  | 14
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 0.5 |  |  |  |  | 5.2
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 1 |  |  |  |  | 2.3
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 5 |  |  |  |  | 1.1
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 10 |  |  |  |  | 0.62
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 50 |  |  |  |  | 0.38
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 100 |  |  |  |  | 0.35
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 500 |  |  |  |  | 0.24
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 200000 |  |  |  |  | 0.24
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 300000 |  |  |  |  | 0.26
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 400000 |  |  |  |  | 0.19
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 500000 |  |  |  |  | 0.14
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 600000 |  |  |  |  | 0.07
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 1000000 |  |  |  |  | 0.07
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 0.1 |  |  |  |  | 19
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 0.5 |  |  |  |  | 7.1
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 1 |  |  |  |  | 3.2
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 5 |  |  |  |  | 1.4
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 10 |  |  |  |  | 0.84
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 50 |  |  |  |  | 0.52
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 100 |  |  |  |  | 0.47
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 500 |  |  |  |  | 0.33
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 200000 |  |  |  |  | 0.33
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 300000 |  |  |  |  | 0.35
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 400000 |  |  |  |  | 0.25
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 500000 |  |  |  |  | 0.19
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 600000 |  |  |  |  | 0.1
A15H1 | A-15 | Obstructions | H | Round | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 1000000 |  |  |  |  | 0.1
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct |  | H (in) | L (in) | d (in) | y (in) | Q (cfm) | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | 0 | [10 empty] | 0.05 | [20 empty] | 0.1 |  |  |  | 1 | 3.9
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct |  | H (mm) | L (mm) | d (mm) | y (mm) | Q (m^3/hr) | N/A | N/A | N/A | [27 empty] | 0.05 | [10 empty] | 0.05 | [20 empty] | 0.5 |  |  |  | 0.97 | 1.5
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.1 | [10 empty] | 0.05 | [20 empty] | 1 |  |  |  | 0.93 | 0.66
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.15 | [10 empty] | 0.05 | [20 empty] | 5 |  |  |  | 0.89 | 0.3
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.2 | [10 empty] | 0.05 | [20 empty] | 10 |  |  |  | 0.84 | 0.17
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.25 | [10 empty] | 0.05 | [20 empty] | 50 |  |  |  | 0.79 | 0.11
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.3 | [10 empty] | 0.05 | [20 empty] | 100 |  |  |  | 0.74 | 0.1
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.35 | [10 empty] | 0.05 | [20 empty] | 500 |  |  |  | 0.67 | 0.07
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [36 empty] | 0.4 | [10 empty] | 0.05 | [20 empty] | 200000 |  |  |  | 0.58 | 0.07
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 300000 |  |  |  |  | 0.07
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 400000 |  |  |  |  | 0.05
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 500000 |  |  |  |  | 0.04
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 600000 |  |  |  |  | 0.02
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.05 | [20 empty] | 1000000 |  |  |  |  | 0.02
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 0.1 |  |  |  |  | 8.4
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 0.5 |  |  |  |  | 3.2
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 1 |  |  |  |  | 1.4
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 5 |  |  |  |  | 0.64
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 10 |  |  |  |  | 0.38
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 50 |  |  |  |  | 0.24
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 100 |  |  |  |  | 0.21
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 500 |  |  |  |  | 0.15
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 200000 |  |  |  |  | 0.15
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 300000 |  |  |  |  | 0.16
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 400000 |  |  |  |  | 0.11
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 500000 |  |  |  |  | 0.09
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 600000 |  |  |  |  | 0.05
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.1 | [20 empty] | 1000000 |  |  |  |  | 0.05
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 0.1 |  |  |  |  | 14
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 0.5 |  |  |  |  | 5.2
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 1 |  |  |  |  | 2.3
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 5 |  |  |  |  | 1.1
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 10 |  |  |  |  | 0.62
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 50 |  |  |  |  | 0.38
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 100 |  |  |  |  | 0.35
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 500 |  |  |  |  | 0.24
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 200000 |  |  |  |  | 0.24
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 300000 |  |  |  |  | 0.26
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 400000 |  |  |  |  | 0.19
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 500000 |  |  |  |  | 0.14
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 600000 |  |  |  |  | 0.07
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.15 | [20 empty] | 1000000 |  |  |  |  | 0.07
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 0.1 |  |  |  |  | 19
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 0.5 |  |  |  |  | 7.1
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 1 |  |  |  |  | 3.2
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 5 |  |  |  |  | 1.4
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 10 |  |  |  |  | 0.84
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 50 |  |  |  |  | 0.52
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 100 |  |  |  |  | 0.47
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 500 |  |  |  |  | 0.33
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 200000 |  |  |  |  | 0.33
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 300000 |  |  |  |  | 0.35
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 400000 |  |  |  |  | 0.25
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 500000 |  |  |  |  | 0.19
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 600000 |  |  |  |  | 0.1
A15H2 | A-15 | Obstructions | H | Rectangular | Smooth Cylinder in Duct | [47 empty] | 0.2 | [20 empty] | 1000000 |  |  |  |  | 0.1
A15I | A-15 | Obstructions | I | Round | Depressed to Avoid an Obstruction |  | D (in) | L (in) | Q (cfm) | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | 0.33 | [35 empty] | 0.24
[7 empty] | D (mm) | L (mm) | Q (m^3/hr) | N/A | N/A | N/A | N/A | N/A
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction |  | W/H - select from list | L/H - select from list | N/A | N/A | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [17 empty] | 1 | 0.125 | [27 empty] | 0.26
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction |  | W/H - select from list | L/H - select from list | N/A | N/A | N/A | N/A | N/A | N/A | [35 empty] | 4 | 0.125 | [27 empty] | 0.1
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 1 | 0.15 | [27 empty] | 0.3
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 4 | 0.15 | [27 empty] | 0.14
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 1 | 0.25 | [27 empty] | 0.33
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 4 | 0.25 | [27 empty] | 0.22
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 1 | 0.3 | [27 empty] | 0.35
A15J | A-15 | Obstructions | J | Rectangular | Depressed to Avoid an Obstruction | [44 empty] | 4 | 0.3 | [27 empty] | 0.3
A15K | A-15 | Obstructions | K | Rectangular | Duct with 4-45° Smooth-radius Ells to Avoid Obstruction |  | input 7: N/A; input 8: N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [35 empty] | 800 | 4 | [9 empty] | 0.18
A15K | A-15 | Obstructions | K | Rectangular | Duct with 4-45° Smooth-radius Ells to Avoid Obstruction |  | input 8: N/A | [53 empty] | 1200 | 6 | [9 empty] | 0.22
A15K | A-15 | Obstructions | K | Rectangular | Duct with 4-45° Smooth-radius Ells to Avoid Obstruction | [62 empty] | 1600 | 8 | [9 empty] | 0.24
A15K | A-15 | Obstructions | K | Rectangular | Duct with 4-45° Smooth-radius Ells to Avoid Obstruction | [62 empty] | 2000 | 10 | [9 empty] | 0.25
A15K | A-15 | Obstructions | K | Rectangular | Duct with 4-45° Smooth-radius Ells to Avoid Obstruction | [62 empty] | 2400 | 12 | [9 empty] | 0.26
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes |  | H | W | B | Q (cfm) | N/A | N/A | N/A | N/A | [8 empty] | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | N/A | N/A | N/A | N/A | N/A | N/A | [18 empty] | 0.5 | [27 empty] | N/A
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes |  | H | W | B | Q (m^3/hr) | N/A | N/A | N/A | N/A | [36 empty] | 1 | [27 empty] | 0.86
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | [45 empty] | 1.5 | [27 empty] | 0.83
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | [45 empty] | 2 | [27 empty] | 0.77
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [45 empty] | 0.5 | [27 empty] | N/A
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [45 empty] | 1 | [27 empty] | 1.85
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [45 empty] | 1.5 | [27 empty] | 2.84
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [45 empty] | 2 | [27 empty] | 2.91
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [45 empty] | 0.5 | [27 empty] | 0.61
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [45 empty] | 1 | [27 empty] | 0.65
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [45 empty] | 1.5 | [27 empty] | N/A
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [45 empty] | 2 | [27 empty] | N/A
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [45 empty] | 0.5 | [27 empty] | 0.88
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [45 empty] | 1 | [27 empty] | 5.26
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [45 empty] | 1.5 | [27 empty] | 6.92
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [45 empty] | 2 | [27 empty] | 7.56
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [45 empty] | 0.5 | [27 empty] | 1.26
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [45 empty] | 1 | [27 empty] | 6.22
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [45 empty] | 1.5 | [27 empty] | 8.82
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [45 empty] | 2 | [27 empty] | 9.24

## Constraints
Duct ID | Entry Key | Constraint Type | Operator | Value | Message
A11P | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A8A | entry_1 | compare_to_entry | < | entry_2 | Upstream diameter must be less than downstream diameter.
A8B | entry_1 | compare_to_entry | < | entry_3 | Upstream height must be less than downstream height.
A8B | entry_2 | compare_to_entry | < | entry_4 | Upstream width must be less than downstream width.
A8E | entry_2 | compare_to_entry | < | entry_1 | Upstream height must be less than downstream height.
A8F | entry_1 | compare_to_entry | < | entry_2 | Upstream height must be less than downstream height.
A8G | entry_1 | compare_to_entry | < | entry_2 | Upstream height must be less than downstream height.
A8H | entry_1 | compare_to_entry | < | entry_2 | Upstream height must be less than downstream height.
A8I | entry_1 | compare_to_entry | < | entry_2 | Upstream height must be less than downstream height.
A8J | entry_2 | compare_to_entry | < | entry_4 | Upstream width must be less than downstream width.
A8J | entry_1 | compare_to_entry | < | entry_3 | Upstream height must be less than downstream height.
A9A1 | entry_2 | compare_to_entry | > | entry_1 | Upstream diameter must be greater than downstream diameter.
A9A2 | entry_3 | compare_to_entry | > | entry_1 | Upstream height must be greater than downstream height.
A9A2 | entry_4 | compare_to_entry | > | entry_2 | Upstream width must be greater than downstream width.
A9B1 | entry_2 | compare_to_entry | > | entry_1 | Upstream diameter must be greater than downstream diameter.
A9B2 | entry_3 | compare_to_entry | > | entry_1 | Upstream height must be greater than downstream height.
A9B2 | entry_4 | compare_to_entry | > | entry_2 | Upstream width must be greater than downstream width.
A9C | entry_1 | compare_to_entry | < | entry_2 | Upstream height must be greater than downstream diameter.
A9C | entry_1 | compare_to_entry | < | entry_3 | Upstream width must be greater than downstream diameter.
A10A1 | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A10B | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A10E | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main upstream diameter.
A10E | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main upstream diameter.
A10E | entry_1 | compare_to_entry | < | entry_2 - 1.9999 | Main upstream diameter must be at least 2 inches smaller than main downstream diameter.
A10H | entry_2 | compare_to_entry | < | entry_4 | Branch width must be less than main downstream width.
A10H | entry_3 | compare_to_entry | < | entry_4 | Main upstream width must be less than main downstream width.
A11A | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11B | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11C | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11D | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11E | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11F | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11G | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11H | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11I | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11J | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11K | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11L | entry_2 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main diameter.
A11M | entry_1 | compare_to_entry | < | entry_2 - 1.9999 | Main downstream diameter must be at least 2 inches smaller than main upstream diameter.
A11M | entry_3 | compare_to_entry | < | entry_2 - 1.9999 | Branch diameter must be at least 2 inches smaller than main upstream diameter.
A11N | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A11O | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A11P | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A11Q | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A11R | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch height must be at least 2 inches smaller than main height.
A11S | entry_3 | compare_to_entry | < | entry_1 - 1.9999 | Branch diameter must be at least 2 inches smaller than main height.
A11U | entry_3 | compare_to_entry | < | entry_2 | Branch diameter must be less than main width.
A11V | entry_3 | compare_to_entry | < | entry_2 | Branch width must be less than main upstream width.
A11V | entry_4 | compare_to_entry | < | entry_2 | Main downstream width must be less than main upstream width.