## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Ab/Ac | Qb/Qc | C
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | D_main (in) | D_branch (in) | Q_s (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.1 | 0.1 | 0.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | D_main (mm) | D_branch (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.1 | 0.2 | 3.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.3 | 9.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.4 | 16
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.5 | 26
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.6 | 37
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.7 | 43
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.8 | 65
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 0.9 | 82
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.1 | 1 | 101
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.1 | -0.37
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.2 | 0.72
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.3 | 2.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.4 | 4.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.5 | 6.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.6 | 9.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.7 | 13
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.8 | 17
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 0.9 | 21
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.2 | 1 | 26
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.1 | -0.51
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.2 | 0.17
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.3 | 1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.4 | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.5 | 3.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.6 | 4.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.7 | 6.3
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.8 | 7.9
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 0.9 | 9.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.3 | 1 | 12
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.1 | -0.46
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.2 | -0.02
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.3 | 0.44
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.4 | 0.94
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.5 | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.6 | 1.6
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.7 | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.8 | 2.7
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 0.9 | 3.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.4 | 1 | 4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.1 | -0.5
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.2 | -0.14
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.3 | 0.21
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.4 | 0.54
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.5 | 0.66
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.6 | 0.92
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.7 | 1.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.8 | 1.5
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 0.9 | 1.8
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.6 | 1 | 2.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.1 | -0.51
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.2 | -0.18
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.3 | 0.11
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.4 | 0.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.5 | 0.49
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.6 | 0.69
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.7 | 0.88
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.8 | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 0.9 | 1.2
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 0.8 | 1 | 1.4
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.1 | -0.52
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.2 | -0.24
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.3 | -0.08
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.4 | 0.32
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.5 | 0.42
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.6 | 0.57
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.7 | 0.72
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.8 | 0.86
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 0.9 | 0.99
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | branch | [14 empty] | 1 | 1 | 1.1
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main |  |  |  |  | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [7 empty] | 0.1 | 0.16
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.2 | 0.27
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.3 | 0.38
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.4 | 0.46
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.5 | 0.53
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.6 | 0.57
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.7 | 0.59
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.8 | 0.6
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 0.9 | 0.59
A10B | A-10 | Converging Junctions (Tees, Wyes) | B | Round | Converging Tee, 90° | main | [15 empty] | 1 | 0.55