## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vc | Qb/Qc | C
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | H_s (in) | W_s (in) | Q_s (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 0.1 | -0.63
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | H_s (mm) | W_s (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0 | 0.2 | -0.55
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.3 | 0.13
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.4 | 0.23
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.5 | 0.78
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.6 | 1.3
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.7 | 1.93
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.8 | 3.1
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 0.9 | 4.88
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 0 | 1 | 5.6
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.1 | -0.49
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.2 | -0.21
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.3 | 0.23
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.4 | 0.6
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.5 | 1.27
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.6 | 2.06
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.7 | 2.75
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.8 | 3.7
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 0.9 | 4.93
A10C | A-10 | Converging Junctions (Tees, Wyes) | C | Rectangular | Converging Tee, Round Branch to Rectangular Main | branch | [14 empty] | 1200 | 1 | 5.95