## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vc | Qb/Qc | C
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | H_s (in) | W_s (in) | Q_s (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 0.1 | -0.75
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | H_s (mm) | W_s (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0 | 0.2 | -0.53
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.3 | -0.03
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.4 | 0.33
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.5 | 1.03
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.6 | 1.1
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.7 | 2.15
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.8 | 2.93
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 0.9 | 4.18
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 0 | 1 | 4.78
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.1 | -0.69
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.2 | -0.21
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.3 | 0.23
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.4 | 0.67
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.5 | 1.17
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.6 | 1.66
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.7 | 2.67
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.8 | 3.36
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 0.9 | 3.93
A10D | A-10 | Converging Junctions (Tees, Wyes) | D | Rectangular | Converging Tee, Rectangular Main & Branch | branch | [14 empty] | 1200 | 1 | 5.13