## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Ab/Ac | As/Ac | Ab/As | Qb/Qc | C
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | H (in) | W_b (in) | W_s (in) | W_c (in) | Q_s (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.25 |  | 0.25 | 0.1 | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | H (mm) | W_b (mm) | W_s (mm) | W_c (mm) | Q_s (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.25 |  | 0.25 | 0.2 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.3 | 0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.4 | 1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.5 | 2.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.6 | 3.7
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.7 | 5.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.8 | 8.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.25 | 0.9 | 11
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.1 | -1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.2 | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.3 | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.4 | 1.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.5 | 3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.6 | 4.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.7 | 6.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.8 | 8.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.25 |  | 0.33 | 0.9 | 11
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.1 | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.2 | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.3 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.4 | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.5 | 0.45
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.6 | 0.7
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.7 | 1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.8 | 1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.5 | 0.9 | 2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.1 | -1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.2 | -0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.3 | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.4 | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.5 | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.6 | 0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.7 | 1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.8 | 1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 0.67 | 0.9 | 2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.1 | -2.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.2 | -1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.3 | -0.95
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.4 | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.5 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.6 | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.7 | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.8 | 1.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 0.5 |  | 1 | 0.9 | 1.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.1 | -0.6
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.2 | -0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.3 | -0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.4 | -0.04
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.5 | 0.13
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.6 | 0.21
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.7 | 0.29
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.8 | 0.36
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1 | 0.9 | 0.42
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.1 | -1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.2 | -0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.3 | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.4 | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.5 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.6 | 0.16
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.7 | 0.24
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.8 | 0.32
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 1.33 | 0.9 | 0.38
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.1 | -2.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.2 | -1.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.3 | -0.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.4 | -0.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.5 | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.6 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.7 | 0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.8 | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | branch | [16 empty] | 1 |  | 2 | 0.9 | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [6 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [6 empty] | 0.25 | 0.75 |  | 0.1 | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.2 | 0.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.3 | 0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.4 | -0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.5 | -0.45
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.6 | -0.92
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.7 | -1.5
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.8 | -0.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.25 | 0.75 |  | 0.9 | -0.26
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.1 | 0.17
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.2 | 0.16
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.3 | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.4 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.5 | -0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.6 | -0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.7 | -0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.8 | -0.37
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 1.05 |  | 0.9 | -0.46
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.1 | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.2 | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.3 | 0.32
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.4 | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.5 | 0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.6 | -0.03
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.7 | -0.23
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.8 | -0.42
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.75 |  | 0.9 | -0.58
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.1 | 1.2
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.2 | 1.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.3 | 0.9
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.4 | 0.65
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.5 | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.6 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.7 | -0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.8 | -0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 0.5 | 0.5 |  | 0.9 | -1.3
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.1 | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.2 | 0.24
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.3 | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.4 | 0.26
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.5 | 0.23
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.6 | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.7 | 0.1
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.8 | 0
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 1 |  | 0.9 | -0.12
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.1 | 0.75
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.2 | 0.36
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.3 | 0.38
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.4 | 0.35
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.5 | 0.27
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.6 | 0.18
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.7 | 0.05
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.8 | -0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.75 |  | 0.9 | -0.22
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.1 | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.2 | 0.87
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.3 | 0.8
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.4 | 0.68
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.5 | 0.55
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.6 | 0.4
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.7 | 0.25
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.8 | 0.08
A10H | A-10 | Converging Junctions (Tees, Wyes) | H | Rectangular | Converging Rectangular Wye | main | [16 empty] | 1 | 0.5 |  | 0.9 | -0.1