## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | dropdown 2 | output 1 | output 2 | output 3 | output 4 | Q_1b/Qc or Q_2b/Qc | ANGLE | C
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | D_branch | θ (degrees) - select from list | Q1b (cfm) | Q2b (cfm) | 15 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 15 | -2.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | D_branch | θ (degrees) - select from list | Q1b (m^3/hr) | Q2b (m^3/hr) | 30 |  |  |  |  | 0 | 30 | -2.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye |  |  |  |  | 45 |  |  |  |  | 0 | 45 | -1.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.1 | 15 | -1.9
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.1 | 30 | -1.5
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.1 | 45 | -0.93
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.2 | 15 | -1.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.2 | 30 | -1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.2 | 45 | -0.55
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.3 | 15 | -0.77
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.3 | 30 | -0.53
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.3 | 45 | -0.16
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.4 | 15 | -0.3
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.4 | 30 | -0.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.4 | 45 | 0.2
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.5 | 15 | 0.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.5 | 30 | 0.28
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.5 | 45 | 0.56
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.6 | 15 | 0.41
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.6 | 30 | 0.69
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.6 | 45 | 0.92
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.7 | 15 | 0.67
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.7 | 30 | 0.91
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.7 | 45 | 1.26
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.8 | 15 | 0.85
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.8 | 30 | 1.1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.8 | 45 | 1.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.9 | 15 | 0.97
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.9 | 30 | 1.4
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 0.9 | 45 | 2
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 1 | 15 | 1
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 1 | 30 | 1.6
A10I1 | A-10 | Converging Junctions (Tees, Wyes) | I | Round | Symmetrical Round Wye | [9 empty] | 1 | 45 | 2.3