## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 3 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Ab/Ac | Vs/Vc | Qb/Qc | C
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | D_c (in) | D_b (in) | Angle - select from list | Q_c (cfm) | Q_b (cfm) |  | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) |  | 0 |  | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | D_c (mm) | D_b (mm) | Angle - select from list | Q_c (m^3/hr) | Q_b (m^3/hr) | [12 empty] | 0.1 |  | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.2 |  | 0.22
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.3 |  | 0.17
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.4 |  | 0.13
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.5 |  | 0.09
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.6 |  | 0.06
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 0.8 |  | 0.02
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, Main | main | [17 empty] | 1 |  | 0
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | D_c (in) | D_b (in) | Angle - select from list | Q_c (cfm) | Q_b (cfm) | 30 | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.8 |  | 0.1 | 0.75
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | D_c (mm) | D_b (mm) | Angle - select from list | Q_c (m^3/hr) | Q_b (m^3/hr) | 45 | [10 empty] | 0.7 |  | 0.1 | 0.72
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [5 empty] | 60 | [10 empty] | 0.6 |  | 0.1 | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [5 empty] | 90 | [10 empty] | 0.5 |  | 0.1 | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.1 | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.1 | 0.55
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.1 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.1 | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.2 | 0.55
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.2 | 0.51
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.2 | 0.46
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.2 | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.2 | 0.33
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.2 | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.2 | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.3 | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.3 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.3 | 0.36
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.3 | 0.31
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.3 | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.3 | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.3 | 0.24
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.3 | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.4 | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.4 | 0.25
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.4 | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.4 | 0.19
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.4 | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.4 | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.4 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.5 | 0.21
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.5 | 0.18
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.5 | 0.17
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.5 | 0.18
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.5 | 0.27
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.5 | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.5 | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.6 | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.6 | 0.15
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.6 | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.6 | 0.22
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.6 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.6 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.7 | 0.15
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.7 | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.7 | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.7 | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.7 | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.7 | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.8 | 0.16
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.8 | 0.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.8 | 0.28
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.8 | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.8 | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.8 |  | 0.9 | 0.19
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.7 |  | 0.9 | 0.26
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.6 |  | 0.9 | 0.39
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.5 |  | 0.9 | 0.67
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.4 |  | 0.9 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.3 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.2 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 30° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) |  |  | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.8 |  | 0.1 | 0.78
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [12 empty] | 0.7 |  | 0.1 | 0.77
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.1 | 0.74
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.1 | 0.71
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.1 | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.1 | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.1 | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.1 | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.2 | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.2 | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.2 | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.2 | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.2 | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.2 | 0.48
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.2 | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.3 | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.3 | 0.49
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.3 | 0.47
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.3 | 0.44
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.3 | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.3 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.3 | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.3 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.4 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.4 | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.4 | 0.37
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.4 | 0.38
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.4 | 0.43
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.4 | 0.73
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.4 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.5 | 0.34
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.5 | 0.34
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.5 | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.5 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.5 | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.5 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.6 | 0.31
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.6 | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.6 | 0.36
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.6 | 0.45
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.6 | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.6 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.7 | 0.32
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.7 | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.7 | 0.43
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.7 | 0.59
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.7 | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.7 | 2.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.8 | 0.35
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.8 | 0.41
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.8 | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.8 | 0.78
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.8 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.8 |  | 0.9 | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.7 |  | 0.9 | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.6 |  | 0.9 | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.5 |  | 0.9 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.4 |  | 0.9 | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.3 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.2 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 45° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) |  |  | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.8 |  | 0.1 | 0.83
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [12 empty] | 0.7 |  | 0.1 | 0.82
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.1 | 0.81
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.1 | 0.79
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.1 | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.1 | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.1 | 0.77
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.1 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.2 | 0.71
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.2 | 0.69
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.2 | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.2 | 0.66
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.2 | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.2 | 0.75
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.2 | 0.96
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.3 | 2.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.3 | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.3 | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.3 | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.3 | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.3 | 0.65
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.3 | 0.89
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.3 | 1.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.4 | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.4 | 0.56
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.4 | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.4 | 0.62
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.4 | 0.74
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.4 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.4 | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.5 | 0.52
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.5 | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.5 | 0.58
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.5 | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.5 | 0.89
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.5 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.6 | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.6 | 0.54
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.6 | 0.61
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.6 | 0.76
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.6 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.6 | 2.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.7 | 0.53
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.7 | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.7 | 0.72
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.7 | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.7 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.7 | 3.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.8 | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.8 | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.8 | 0.87
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.8 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.8 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.8 |  | 0.9 | 0.68
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.7 |  | 0.9 | 0.82
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.6 |  | 0.9 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.5 |  | 0.9 | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.4 |  | 0.9 | 2.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.3 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.2 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 60° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) |  |  | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.8 |  | 0.1 | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [12 empty] | 0.7 |  | 0.1 | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.1 | 0.96
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.1 | 0.97
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.1 | 0.99
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.1 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.1 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.1 | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.2 | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.2 | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.2 | 0.97
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.2 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.2 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.2 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.2 | 1.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.3 | 0.92
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.3 | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.3 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.3 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.3 | 1.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.3 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.3 | 2.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.4 | 0.93
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.4 | 0.98
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.4 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.4 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.4 | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.4 | 2.3
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.5 | 0.94
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.5 | 1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.5 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.5 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.5 | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.6 | 0.95
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.6 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.6 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.6 | 1.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.6 | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.7 | 1.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.7 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.7 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.7 | 1.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.7 | 2.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.8 | 1.2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.8 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.8 | 1.7
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.8 | 2.1
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.8
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.8 |  | 0.9 | 1.4
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.7 |  | 0.9 | 1.6
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.6 |  | 0.9 | 2
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.5 |  | 0.9 | 2.5
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.4 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.3 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.2 |  | 0.9
A11A | A-11 | Diverging Junctions (Tees, Wyes) | A | Round | Tee or Wye, 90° | branch | [16 empty] | 0.1 |  | 0.9