## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | C
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 1
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.2 | 0.84
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 0.4 | 0.61
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 0.6 | 0.41
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 0.8 | 0.27
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 1 | 0.17
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 1.2 | 0.12
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 1.4 | 0.12
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 1.6 | 0.14
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 1.8 | 0.18
A11C | A-11 | Diverging Junctions (Tees, Wyes) | C | Round | Conical Wye, 45° | branch | [14 empty] | 2 | 0.27