## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | C
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 1
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.2 | 0.88
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 0.4 | 0.77
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 0.6 | 0.68
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 0.8 | 0.65
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 1 | 0.69
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 1.2 | 0.73
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 1.4 | 0.88
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 1.6 | 1.14
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 1.8 | 1.54
A11I | A-11 | Diverging Junctions (Tees, Wyes) | I | Round | 45° Wye, Rolled 45° with 60° Elbow, Branch 90° to Main | branch | [14 empty] | 2 | 2.2