## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | C
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 1
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | D_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.2 | 0.93
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 0.4 | 0.71
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 0.6 | 0.55
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 0.8 | 0.44
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 1 | 0.42
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 1.2 | 0.42
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 1.4 | 0.44
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 1.6 | 0.47
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 1.8 | 0.54
A11L | A-11 | Diverging Junctions (Tees, Wyes) | L | Round | 45° Conical Wye, Rolled 45° with 30° Elbow, Branch 45° to Main | branch | [14 empty] | 2 | 0.62