## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Vs/Vc | C
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | D_c (in) | D_b (in) | D_s (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 |  | 0.76
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | D_c (mm) | D_b (mm) | D_s (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 |  | 0.6
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 0.6 |  | 0.52
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 0.7 |  | 0.5
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 0.8 |  | 0.51
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 0.9 |  | 0.52
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1 |  | 0.56
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1.1 |  | 0.61
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1.2 |  | 0.68
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1.4 |  | 0.86
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1.6 |  | 1.1
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 1.8 |  | 1.4
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 2 |  | 1.8
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 2.2 |  | 2.2
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 2.4 |  | 2.6
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 2.6 |  | 3.1
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 2.8 |  | 3.7
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | branch | [15 empty] | 3 |  | 4.2
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 0.2 | 0.14
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 0.4 | 0.06
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 0.6 | 0.05
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 0.8 | 0.09
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 1 | 0.18
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 1.2 | 0.3
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 1.4 | 0.46
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 1.6 | 0.64
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 1.8 | 0.84
A11M | A-11 | Diverging Junctions (Tees, Wyes) | M | Round | 45° Conical Main & Branch with 45° Elbow, Branch 90° to Main | main | [16 empty] | 2 | 1