## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Qb/Qc | C
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.1 | 0.91
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 | 0.1 | 0.81
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.1 | 0.77
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.1 | 0.78
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.1 | 0.78
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.1 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.1 | 1.19
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.1 | 1.35
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.1 | 1.44
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.2
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.2 | 0.79
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.2 | 0.72
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.2 | 0.73
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.2 | 0.98
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.2 | 1.11
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.2 | 1.22
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.2 | 1.42
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.2 | 1.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.3
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.3
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.3 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.3 | 0.69
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.3 | 0.85
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.3 | 1.16
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.3 | 1.26
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.3 | 1.55
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.3 | 1.75
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.4
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.4
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.4
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.4 | 0.66
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.4 | 0.79
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.4 | 1.23
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.4 | 1.29
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.4 | 1.59
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.4 | 1.74
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.5 | 0.74
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.5 | 1.03
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.5 | 1.54
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.5 | 1.63
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.5 | 1.72
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.6
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.6
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.6
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.6
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.6
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.6 | 0.86
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.6 | 1.25
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.6 | 1.5
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.6 | 2.24
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.7
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.7 | 0.92
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.7 | 1.31
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.7 | 1.63
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.8
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.8 | 1.09
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.8 | 1.4
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.2 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.4 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.6 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 0.8 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.2 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.4 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.6 | 0.9
A11N | A-11 | Diverging Junctions (Tees, Wyes) | N | Rectangular | Tee, 45° Rectangular Main & Branch | branch | [16 empty] | 1.8 | 0.9 | 1.17