## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Qb/Qc | C
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.1 | 0.61
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 | 0.1 | 0.46
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.1 | 0.43
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.1 | 0.39
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.1 | 0.34
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.1 | 0.37
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.1 | 0.57
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.1 | 0.89
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.1 | 1.33
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.2
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.2 | 0.61
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.2 | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.2 | 0.43
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.2 | 0.57
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.2 | 0.64
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.2 | 0.71
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.2 | 1.08
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.2 | 1.34
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.3
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.3
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.3 | 0.54
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.3 | 0.62
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.3 | 0.77
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.3 | 0.85
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.3 | 1.04
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.3 | 1.28
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.3 | 2.04
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.4
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.4
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.4
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.4 | 0.53
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.4 | 0.73
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.4 | 0.98
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.4 | 1.16
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.4 | 1.3
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.4 | 1.78
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.5
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.5 | 0.68
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.5 | 1.07
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.5 | 1.54
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.5 | 1.69
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.5 | 1.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.6
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.6
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.6
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.6
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.6
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.6 | 0.83
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.6 | 1.36
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.6 | 2.09
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.6 | 2.4
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.7
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.7 | 1.18
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.7 | 1.81
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.7 | 2.77
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.8
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.8 | 1.47
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.8 | 2.23
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.9
A11O | A-11 | Diverging Junctions (Tees, Wyes) | O | Rectangular | Tee, 45° Entry, Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.9 | 1.92