## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Qb/Qc | C
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.1 | 0.58
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 | 0.1 | 0.67
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.1 | 0.78
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.1 | 0.88
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.1 | 1.12
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.1 | 1.49
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.1 | 2.1
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.1 | 2.72
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.1 | 3.42
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.2
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.2 | 0.64
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.2 | 0.76
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.2 | 0.98
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.2 | 1.05
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.2 | 1.48
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.2 | 2.21
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.2 | 3.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.2 | 4.58
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.3 | 0.75
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.3 | 0.81
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.3 | 1.08
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.3 | 1.4
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.3 | 2.25
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.3 | 2.84
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.3 | 3.65
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.4
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.4
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.4
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.4 | 1.01
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.4 | 1.18
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.4 | 1.51
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.4 | 2.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.4 | 3.09
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.4 | 3.92
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.5
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.5
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.5
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.5
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.5 | 1.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.5 | 1.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.5 | 2.32
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.5 | 3.3
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.5 | 4.2
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.6
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.6
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.6
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.6
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.6
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.6 | 1.91
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.6 | 2.48
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.6 | 3.19
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.6 | 4.15
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.7
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.7 | 2.53
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.7 | 3.29
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.7 | 4.14
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.8
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.8 | 3.16
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.8 | 4.1
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.2 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.4 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.6 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 0.8 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.2 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.4 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.6 | 0.9
A11Q | A-11 | Diverging Junctions (Tees, Wyes) | Q | Rectangular | Tee Rectangular Main & Branch with Damper | branch | [16 empty] | 1.8 | 0.9 | 4.05