## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Qb/Qc | C
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.1 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 | 0.1 | 0.62
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.1 | 0.74
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.1 | 0.99
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.1 | 1.48
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.1 | 1.91
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.1 | 2.47
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.1 | 3.17
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.1 | 3.85
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.2
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.2 | 0.69
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.2 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.2 | 1.1
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.2 | 1.12
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.2 | 1.33
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.2 | 1.67
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.2 | 2.4
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.2 | 3.37
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.3 | 0.82
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.3 | 0.95
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.3 | 1.41
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.3 | 1.43
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.3 | 1.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.3 | 2.33
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.3 | 2.89
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.4
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.4
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.4
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.4 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.4 | 1.24
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.4 | 1.52
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.4 | 2.04
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.4 | 2.53
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.4 | 3.23
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.5
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.5
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.5
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.5
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.5 | 1.21
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.5 | 1.55
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.5 | 1.86
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.5 | 2.31
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.5 | 3.09
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.6
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.6 | 1.64
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.6 | 1.98
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.6 | 2.51
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.6 | 3.03
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.7
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.7 | 2.47
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.7 | 3.13
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.7 | 3.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.8
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.8 | 3.25
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.8 | 3.74
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.2 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.4 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.6 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 0.8 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.2 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.4 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.6 | 0.9
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | branch | [16 empty] | 1.8 | 0.9 | 4.11
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [6 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [6 empty] | 0.2 |  | 0.03
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 0.4 |  | 0.04
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 0.6 |  | 0.07
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 0.8 |  | 0.12
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 1 |  | 0.13
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 1.2 |  | 0.14
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 1.4 |  | 0.27
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 1.6 |  | 0.3
A11R | A-11 | Diverging Junctions (Tees, Wyes) | R | Rectangular | Tee Rectangular Main & Branch with Extractor | main | [16 empty] | 1.8 |  | 0.25