## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Vb/Vc | Qb/Qc | C
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | H_c (in) | W_c (in) | D_b (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.1 | 1
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | H_c (mm) | W_c (mm) | D_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.4 | 0.1 | 1.01
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.1 | 1.14
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.1 | 1.18
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.1 | 1.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.1 | 1.46
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.1 | 1.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.1 | 1.93
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.1 | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.2 | 1.07
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.2 | 1.1
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.2 | 1.31
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.2 | 1.38
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.2 | 1.58
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.2 | 1.82
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.2 | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.2 | 2.17
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.3
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.3 | 1.08
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.3 | 1.12
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.3 | 1.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.3 | 1.45
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.3 | 1.65
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.3 | 2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.3 | 2.2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.4
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.4 | 1.13
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.4 | 1.23
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.4 | 1.31
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.4 | 1.51
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.4 | 1.85
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.4 | 2.13
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.5
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.5 | 1.26
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.5 | 1.39
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.5 | 1.56
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.5 | 1.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.5 | 2.06
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.6
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.6 | 1.48
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.6 | 1.64
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.6 | 1.76
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.6 | 1.98
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.7
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.7 | 1.71
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.7 | 1.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.7 | 1.99
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.8
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.8 | 1.88
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.8 | 2
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.2 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.4 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.6 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 0.8 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.2 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.4 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.6 | 0.9
A11S | A-11 | Diverging Junctions (Tees, Wyes) | S | Rectangular | Tee Rectangular Main to Round Branch | branch | [15 empty] | 1.8 | 0.9 | 2.07