## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 6 | output 1 | output 2 | output 3 | output 4 | As/Ac | Vb/Vc | Vs/Vc | ANGLE | C
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | H (in) | W_c (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Angle | 15 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) |  | 0.1 |  | 15 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [6 empty] | 30 | [5 empty] | 0.1 |  | 30 | 0.84
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [6 empty] | 45 | [5 empty] | 0.1 |  | 45 | 0.87
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [6 empty] | 60 | [5 empty] | 0.1 |  | 60 | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [6 empty] | 90 | [5 empty] | 0.1 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.2 |  | 15 | 0.65
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.2 |  | 30 | 0.69
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.2 |  | 45 | 0.74
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.2 |  | 60 | 0.82
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.2 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.3 |  | 15 | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.3 |  | 30 | 0.56
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.3 |  | 45 | 0.63
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.3 |  | 60 | 0.79
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.3 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.4 |  | 15 | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.4 |  | 30 | 0.44
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.4 |  | 45 | 0.54
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.4 |  | 60 | 0.66
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.4 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.5 |  | 15 | 0.28
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.5 |  | 30 | 0.34
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.5 |  | 45 | 0.45
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.5 |  | 60 | 0.59
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.5 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.6 |  | 15 | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.6 |  | 30 | 0.26
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.6 |  | 45 | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.6 |  | 60 | 0.53
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.6 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.8 |  | 15 | 0.11
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.8 |  | 30 | 0.19
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.8 |  | 45 | 0.29
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.8 |  | 60 | 0.43
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 0.8 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1 |  | 15 | 0.06
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1 |  | 30 | 0.15
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1 |  | 45 | 0.24
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1 |  | 60 | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.2 |  | 15 | 0.14
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.2 |  | 30 | 0.15
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.2 |  | 45 | 0.23
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.2 |  | 60 | 0.33
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.2 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.4 |  | 15 | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.4 |  | 30 | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.4 |  | 45 | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.4 |  | 60 | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.4 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.6 |  | 15 | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.6 |  | 30 | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.6 |  | 45 | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.6 |  | 60 | 0.51
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.6 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.8 |  | 15 | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.8 |  | 30 | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.8 |  | 45 | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.8 |  | 60 | 0.76
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 1.8 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 2 |  | 15 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 2 |  | 30 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 2 |  | 45 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 2 |  | 60 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | branch | [12 empty] | 2 |  | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [7 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 - 1.0 |  | 0 | 15-60 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.1 | 15-60 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.2 | 15-60 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.3 | 15-60 | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.4 | 15-60 | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.5 | 15-60 | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.6 | 15-60 | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 0.8 | 15-60 | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 1 | 15-60 | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 1.2 | 15-60 | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 1.4 | 15-60 | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 1.6 | 15-60 | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 1.8 | 15-60 | 1.8
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 1.0 |  | 2 | 15-60 | 3.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0 | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.1 | 90 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.2 | 90 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.3 | 90 | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.4 | 90 | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.5 | 90 | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.6 | 90 | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 0.8 | 90 | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 1 | 90 | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 1.2 | 90 | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 1.4 | 90 | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 1.6 | 90 | 0.9
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 1.8 | 90 | 1.8
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0 - 0.4 |  | 2 | 90 | 3.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0 | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.1 | 90 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.2 | 90 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.3 | 90 | 0.52
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.4 | 90 | 0.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.5 | 90 | 0.3
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.6 | 90 | 0.23
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 0.8 | 90 | 0.17
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 1 | 90 | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 1.2 | 90 | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 1.4 | 90 | 0.79
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 1.6 | 90 | 1.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 1.8 | 90 | 2.4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.5 |  | 2 | 90 | 4
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0 | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.1 | 90 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.2 | 90 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.3 | 90 | 0.52
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.4 | 90 | 0.38
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.5 | 90 | 0.28
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.6 | 90 | 0.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 0.8 | 90 | 0.1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 1 | 90 | 0.1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 1.2 | 90 | 0.21
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 1.4 | 90 | 0.59
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 1.6 | 90 | 1.2
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 1.8 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.6 |  | 2 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0 | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.1 | 90 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.2 | 90 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.3 | 90 | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.4 | 90 | 0.37
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.5 | 90 | 0.27
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.6 | 90 | 0.18
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 0.8 | 90 | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 1 | 90 | 0.05
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 1.2 | 90 | 0.14
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 1.4 | 90 | 0.39
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 1.6 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 1.8 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | 0.7 |  | 2 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0 | 90 | 1
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.1 | 90 | 0.81
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.2 | 90 | 0.64
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.3 | 90 | 0.5
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.4 | 90 | 0.36
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.5 | 90 | 0.25
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.6 | 90 | 0.16
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 0.8 | 90 | 0.04
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 1 | 90 | 0
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 1.2 | 90 | 0.07
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 1.4 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 1.6 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 1.8 | 90
A11T | A-11 | Diverging Junctions (Tees, Wyes) | T | Rectangular | Rectangular Wye | main | [11 empty] | >=0.8 |  | 2 | 90