## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 9 | output 10 | Ab/Ac | Ab/As | Qb/Qc | C
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | H (in) | W_c (in) | W_b (in) | W_s (in) | Q_c (cfm) | Q_b (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.25 | 0.25 | 0.1 | 0.55
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | H (mm) | W_c (mm) | W_b (mm) | W_s (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | [10 empty] | 0.25 | 0.33 | 0.1 | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.1 | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.1 | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.1 | 0.44
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.1 | 0.67
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.1 | 0.7
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.1 | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.2 | 0.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.2 | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.2 | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.2 | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.2 | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.2 | 0.55
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.2 | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.2 | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.3 | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.3 | 0.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.3 | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.3 | 0.32
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.3 | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.3 | 0.46
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.3 | 0.51
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.3 | 0.43
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.4 | 0.85
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.4 | 0.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.4 | 0.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.4 | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.4 | 0.41
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.4 | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.4 | 0.42
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.4 | 0.33
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.5 | 1.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.5 | 1.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.5 | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.5 | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.5 | 0.52
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.5 | 0.32
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.5 | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.5 | 0.24
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.6 | 1.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.6 | 2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.6 | 0.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.6 | 0.44
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.6 | 0.68
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.6 | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.6 | 0.28
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.6 | 0.17
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.7 | 3.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.7 | 2.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.7 | 0.78
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.7 | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.7 | 0.92
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.7 | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.7 | 0.26
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.7 | 0.15
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.8 | 4.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.8 | 3.8
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.8 | 1.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.8 | 0.92
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.8 | 1.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.8 | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.8 | 0.26
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.8 | 0.17
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.25 | 0.9 | 6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.25 | 0.33 | 0.9 | 5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.5 | 0.9 | 1.5
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 0.67 | 0.9 | 1.4
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 0.5 | 1 | 0.9 | 1.6
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1 | 0.9 | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 1.33 | 0.9 | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | branch | [16 empty] | 1 | 2 | 0.9 | 0.21
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [6 empty] | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | [6 empty] | 0.25 | 0.25 | 0.1 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.1 | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.1 | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.1 | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.1 | 0.72
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.1 | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.1 | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.1 | 0.62
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.2 | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.2 | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.2 | -0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.2 | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.2 | 0.48
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.2 | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.2 | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.2 | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.3 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.3 | -0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.3 | -0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.3 | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.3 | 0.28
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.3 | -0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.3 | 0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.3 | 0.23
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.4 | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.4 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.4 | 0
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.4 | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.4 | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.4 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.4 | -0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.4 | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.5 | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.5 | 0.02
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.5 | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.5 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.5 | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.5 | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.5 | -0.01
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.5 | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.6 | 0.21
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.6 | 0.08
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.6 | 0.12
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.6 | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.6 | 0.04
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.6 | 0.13
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.6 | 0.03
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.6 | 0.05
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.7 | 0.29
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.7 | 0.16
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.7 | 0.19
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.7 | 0.12
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.7 | 0.09
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.7 | 0.22
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.7 | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.7 | 0.06
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.8 | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.8 | 0.24
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.8 | 0.27
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.8 | 0.23
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.8 | 0.18
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.8 | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.8 | 0.2
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.8 | 0.1
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.25 | 0.9 | 0.46
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.25 | 0.33 | 0.9 | 0.34
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.5 | 0.9 | 0.35
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 0.67 | 0.9 | 0.37
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 0.5 | 1 | 0.9 | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1 | 0.9 | 0.38
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 1.33 | 0.9 | 0.3
A11V | A-11 | Diverging Junctions (Tees, Wyes) | V | Rectangular | 90° Curved Rectangular Wye | main | [16 empty] | 1 | 2 | 0.9 | 0.2