## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 3 | output 1 | output 2 | output 3 | output 4 | V_1b/Vc or V_2b/Vc | ANGLE | C
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | H (in) | W_c (in) | θ (degrees) | Qb1 (cfm) | Qb2 (cfm) | 15 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.1 | 15 | 0.81
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | H (mm) | W_c (mm) | θ (degrees) | Qb1 (m^3/hr) | Qb2 (m^3/hr) | 30 |  |  |  |  | 0.1 | 30 | 0.84
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [5 empty] | 45 |  |  |  |  | 0.1 | 45 | 0.87
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [5 empty] | 60 |  |  |  |  | 0.1 | 60 | 0.9
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [5 empty] | 90 |  |  |  |  | 0.1 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.2 | 15 | 0.65
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.2 | 30 | 0.69
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.2 | 45 | 0.74
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.2 | 60 | 0.82
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.2 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.3 | 15 | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.3 | 30 | 0.56
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.3 | 45 | 0.63
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.3 | 60 | 0.79
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.3 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.4 | 15 | 0.38
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.4 | 30 | 0.44
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.4 | 45 | 0.54
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.4 | 60 | 0.66
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.4 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.5 | 15 | 0.28
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.5 | 30 | 0.34
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.5 | 45 | 0.45
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.5 | 60 | 0.59
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.5 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.6 | 15 | 0.2
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.6 | 30 | 0.26
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.6 | 45 | 0.38
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.6 | 60 | 0.53
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.6 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.8 | 15 | 0.11
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.8 | 30 | 0.19
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.8 | 45 | 0.29
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.8 | 60 | 0.43
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 0.8 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1 | 15 | 0.06
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1 | 30 | 0.15
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1 | 45 | 0.24
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1 | 60 | 0.36
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.2 | 15 | 0.14
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.2 | 30 | 0.15
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.2 | 45 | 0.23
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.2 | 60 | 0.36
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.2 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.4 | 15 | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.4 | 30 | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.4 | 45 | 0.3
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.4 | 60 | 0.39
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.4 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.6 | 15 | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.6 | 30 | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.6 | 45 | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.6 | 60 | 0.51
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.6 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.8 | 15 | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.8 | 30 | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.8 | 45 | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.8 | 60 | 0.76
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 1.8 | 90 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 2 | 15 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 2 | 30 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 2 | 45 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 2 | 60 | 1
A11X | A-11 | Diverging Junctions (Tees, Wyes) | X | Rectangular | Wye, Rectangular & Round | [10 empty] | 2 | 90 | 1