## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | PATH | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | input 7 | output 1 | output 2 | output 3 | output 4 | output 5 | output 6 | output 7 | output 8 | output 10 | Qb/Qc | Qs/Qc | C
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | H_c (in) | W_c (in) | H_b (in) | W_b (in) | Q_c (cfm) | Q_b (cfm) | Q_s (cfm) | Branch | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | Main | Loss Coefficient | Fitting Loss (in w.c.) | Vel Pres. at Vₒ (Pv, in. wc) | 0.1 |  | 1.16
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | H_c (mm) | W_c (mm) | H_b (mm) | W_b (mm) | Q_c (m^3/hr) | Q_b (m^3/hr) | Q_s (m^3/hr) | [9 empty] | 0.2 |  | 0.96
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.3 |  | 0.82
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.4 |  | 0.68
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.5 |  | 0.56
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.6 |  | 0.49
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.7 |  | 0.47
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.8 |  | 0.48
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 0.9 |  | 0.5
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | branch | [16 empty] | 1 |  | 0.54
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.1 | 0.21
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.2 | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.3 | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.4 | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.5 | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.6 | 0.2
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.7 | 0.22
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.8 | 0.25
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 0.9 | 0.35
A11Y | A-11 | Diverging Junctions (Tees, Wyes) | Y | Rectangular | Tee, Reducing, 45° Entry Branch | main | [17 empty] | 1 | 0.53