## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 5 | output 1 | output 2 | output 3 | output 4 | t/D | L/D | C
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | t (in) | L (in) | D (in) | Q (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 0 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | t (mm) | L (mm) | D (mm) | Q (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 0.02 | 0 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [5 empty] | perforated plate |  |  |  |  | 0.05 | 0 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 0.002 | 0.57
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 0.002 | 0.51
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 0.002 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 0.01 | 0.68
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 0.01 | 0.52
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 0.01 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 0.05 | 0.8
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 0.05 | 0.55
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 0.05 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 0.2 | 0.92
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 0.2 | 0.66
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 0.2 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 0.5 | 1
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 0.5 | 0.72
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 0.5 | 0.5
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0 | 1 | 1
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.02 | 1 | 0.72
A12A1 | A-12 | Entries | A | Round | Round Duct Mounted in Wall | [10 empty] | 0.05 | 1 | 0.5