## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | input 7 | dropdown 7 | output 1 | output 2 | output 3 | output 4 | L/D | ANGLE | C
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | L (in) | H (in) | W (in) | Hₛ (in) | Wₛ (in) | Q (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.025 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | L (mm) | H (mm) | W (mm) | Hₛ (mm) | Wₛ (mm) | Q (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 0.05 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 0 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 10 | 0.47
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 10 | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 10 | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 10 | 0.39
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 10 | 0.37
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 10 | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 20 | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 20 | 0.41
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 20 | 0.35
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 20 | 0.32
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 20 | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 20 | 0.18
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 30 | 0.43
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 30 | 0.36
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 30 | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 30 | 0.25
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 30 | 0.2
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 30 | 0.13
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 40 | 0.41
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 40 | 0.33
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 40 | 0.26
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 40 | 0.22
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 40 | 0.16
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 40 | 0.11
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 60 | 0.4
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 60 | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 60 | 0.23
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 60 | 0.18
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 60 | 0.15
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 60 | 0.12
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 100 | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 100 | 0.35
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 100 | 0.3
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 100 | 0.27
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 100 | 0.25
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 100 | 0.23
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 140 | 0.45
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 140 | 0.42
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 140 | 0.4
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 140 | 0.38
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 140 | 0.37
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 140 | 0.36
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.025 | 180 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.05 | 180 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.075 | 180 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.1 | 180 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.15 | 180 | 0.5
A12E2 | A-12 | Entries | E | Rectangular | Conical Converging Bellmouth, with End Wall | [12 empty] | 0.6 | 180 | 0.5