## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 4 | dropdown 6 | output 1 | output 2 | output 3 | output 4 | L/D | ANGLE | C
A12F | A-12 | Entries | F | Round | Intake Hood | L (in) | D (in) | Dₛ (in) | θ (degrees) - select from list | Q (cfm) | obstruction - select from list | 0 | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.1 | 0 | 2.6
A12F | A-12 | Entries | F | Round | Intake Hood | L (mm) | D (mm) | Dₛ (mm) | θ (degrees) | Q (m^3/hr) | obstruction - select from list | 15 | screen |  |  |  |  | 0.1 | 15 | 1.3
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.2 | 0 | 1.8
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.2 | 15 | 0.77
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.3 | 0 | 1.5
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.3 | 15 | 0.6
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.4 | 0 | 1.4
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.4 | 15 | 0.48
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.5 | 0 | 1.3
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.5 | 15 | 0.41
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.6 | 0 | 1.2
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.6 | 15 | 0.3
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.7 | 0 | 1.2
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.7 | 15 | 0.29
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.8 | 0 | 1.1
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.8 | 15 | 0.28
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.9 | 0 | 1.1
A12F | A-12 | Entries | F | Round | Intake Hood | [12 empty] | 0.9 | 15 | 0.25