## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 6 | output 1 | output 2 | output 3 | output 4 | As/A | ANGLE | C
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | H (in) | Hₛ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 2 | 14 | 0.37
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | H (mm) | Hₛ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 4 | 14 | 0.25
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 14 | 0.28
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 2 | 20 | 0.38
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 4 | 20 | 0.37
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 20 | 0.47
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 2 | 30 | 0.5
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 4 | 30 | 0.57
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 30 | 0.64
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 2 | 45 | 0.75
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 4 | 45 | 0.82
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 45 | 0.87
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 2 | 60 | 0.9
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 4 | 60 | 1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 60 | 1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 2 | 90 | 1.1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 4 | 90 | 1.1
A13C | A-13 | Exits | C | Rectangular | Plane Diffuser, With or without a Wall | [11 empty] | 6 | 90 | 1.1