## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 5 | output 1 | output 2 | output 3 | output 4 | L/W | R/W | C
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | H (in) | W (in) | L (in) | R (in) | Q (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 0 | 3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | H (mm) | W (mm) | L (mm) | R (mm) | Q (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 0 | 0.75 | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0 | 1 | 1.8
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0 | 1.5 | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0 | 2.5 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0.5 | 0 | 3.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0.5 | 0.75 | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0.5 | 1 | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0.5 | 1.5 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 0.5 | 2.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1 | 0 | 3.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1 | 0.75 | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1 | 1 | 1.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1 | 2.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1.5 | 0 | 3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1.5 | 0.75 | 1.8
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1.5 | 1 | 1.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1.5 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 1.5 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 2 | 0 | 2.7
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 2 | 0.75 | 1.7
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 2 | 1 | 1.3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 2 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 2 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 3 | 0 | 2.4
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 3 | 0.75 | 1.6
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 3 | 1 | 1.3
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 3 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 3 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 4 | 0 | 2.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 4 | 0.75 | 1.6
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 4 | 1 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 4 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 4 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 6 | 0 | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 6 | 0.75 | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 6 | 1 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 6 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 6 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 8 | 0 | 2.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 8 | 0.75 | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 8 | 1 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 8 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 8 | 2.5 | 1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 12 | 0 | 2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 12 | 0.75 | 1.5
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 12 | 1 | 1.2
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 12 | 1.5 | 1.1
A13E2 | A-13 | Exits | E | Rectangular | Discharge to Atmosphere from a 90° Elbow | [11 empty] | 12 | 2.5 | 1