## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 6 | output 1 | output 2 | output 3 | output 4 | H/W | V/V0 | ANGLE | C
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | H (in) | W (in) | θ (degrees) | V (fps) | Q_0 (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.1-0.2 | 0 | 90 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | H (mm) | W (mm) | θ (degrees) | V (m/s) | Q_0 (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 0.1-0.2 | 0 | 120 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 0 | 150 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 0.5 | 90 | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 0.5 | 120 | 0.92
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 0.5 | 150 | 0.75
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1 | 90 | 1.2
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1 | 120 | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1 | 150 | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1.5 | 90 | 1.5
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1.5 | 120 | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 1.5 | 150 | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 2 | 90 | 1.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 2 | 120 | 1.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.1-0.2 | 2 | 150 | 1.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0 | 45 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0 | 60 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0 | 90 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0 | 120 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0 | 150 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0.5 | 45 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0.5 | 60 | 0.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0.5 | 90 | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0.5 | 120 | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 0.5 | 150 | 0.82
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1 | 45 | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1 | 60 | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1 | 90 | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1 | 120 | 0.95
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1 | 150 | 0.83
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1.5 | 45 | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1.5 | 60 | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1.5 | 90 | 1.4
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1.5 | 120 | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 1.5 | 150 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 2 | 45 | 1.6
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 2 | 60 | 1.6
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 2 | 90 | 1.7
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 2 | 120 | 1.7
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 0.5-2.0 | 2 | 150 | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0 | 45 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0 | 60 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0 | 90 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0 | 120 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0.5 | 45 | 0.92
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0.5 | 60 | 0.87
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0.5 | 90 | 0.82
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 0.5 | 120 | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1 | 45 | 0.93
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1 | 60 | 0.87
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1 | 90 | 0.8
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1 | 120 | 0.76
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1.5 | 45 | 1.1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1.5 | 60 | 1
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1.5 | 90 | 0.97
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 1.5 | 120 | 0.9
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 2 | 45 | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 2 | 60 | 1.3
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 2 | 90 | 1.2
A13F1 | A-13 | Exits | F | Rectangular | Duct flush with Wall, Flow along Wall | [11 empty] | 5--10 | 2 | 120 | 0.98