## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 5 | output 1 | output 2 | output 3 | output 4 | V/V0 | ANGLE | C
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | D (in) | θ (degrees) | V (fpm) | Q_0 (cfm) | obstruction - select from type | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0 | 45 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | D (mm) | θ (degrees) | V (m/s) | Q_0 (m^3/hr) | obstruction - select from type | screen |  |  |  |  | 0 | 60 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0 | 90 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0 | 120 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0 | 150 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0.5 | 45 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0.5 | 60 | 0.9
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0.5 | 90 | 0.8
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0.5 | 120 | 0.8
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 0.5 | 150 | 0.82
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1 | 45 | 1.1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1 | 60 | 1.1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1 | 90 | 0.95
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1 | 120 | 0.95
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1 | 150 | 0.83
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1.5 | 45 | 1.3
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1.5 | 60 | 1.4
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1.5 | 90 | 1.4
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1.5 | 120 | 1.3
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 1.5 | 150 | 1
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 2 | 45 | 1.6
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 2 | 60 | 1.6
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 2 | 90 | 1.7
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 2 | 120 | 1.7
A13F2 | A-13 | Exits | F | Round | Duct flush with Wall, Flow along Wall | [10 empty] | 2 | 150 | 1.3