## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 7 | output 1 | output 2 | output 3 | output 4 | A1/A | ANGLE | C
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | H (in) | W (in) | H₁ (in) | angle (deg) | Q (cfm) | obstruction - select from list | none (open) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 1.5 | 10 | 0.51
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | H (mm) | W (mm) | H₁ (mm) | angle (deg) | Q (m^3/hr) | obstruction - select from list | screen |  |  |  |  | 1.5 | 15 | 0.54
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 1.5 | 20 | 0.55
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 1.5 | 25 | 0.59
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 1.5 | 30 | 0.63
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 1.5 | 35 | 0.65
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 10 | 0.34
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 15 | 0.36
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 20 | 0.38
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 25 | 0.43
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 30 | 0.5
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2 | 35 | 0.56
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 10 | 0.25
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 15 | 0.27
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 20 | 0.31
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 25 | 0.37
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 30 | 0.46
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 2.5 | 35 | 0.53
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 10 | 0.21
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 15 | 0.24
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 20 | 0.27
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 25 | 0.35
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 30 | 0.44
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3 | 35 | 0.52
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 10 | 0.18
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 15 | 0.22
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 20 | 0.25
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 25 | 0.33
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 30 | 0.43
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 3.5 | 35 | 0.51
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 10 | 0.17
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 15 | 0.2
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 20 | 0.24
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 25 | 0.33
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 30 | 0.42
A13G | A-13 | Exits | G | Rectangular | Plane Asymmetric Diffuser at Fan Outlet without Ductwork | [11 empty] | 4 | 35 | 0.5