## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | input 7 | output 1 | output 2 | output 3 | output 4 | A1/A | ANGLE | C
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | H (in) | W (in) | H₁ (in) | W₁ (in) | L (in) | Q (cfm) | obstruction - select from list | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 1.5 | 10 | 0.54
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | L (mm) | Q (m^3/hr) | obstruction - select from list |  |  |  |  | 1.5 | 15 | 0.67
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 1.5 | 20 | 0.45
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 1.5 | 25 | 0.8
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 1.5 | 30 | 0.85
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2 | 10 | 0.42
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2 | 15 | 0.58
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2 | 20 | 0.67
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2 | 25 | 0.74
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2 | 30 | 0.78
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2.5 | 10 | 0.37
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2.5 | 15 | 0.53
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2.5 | 20 | 0.65
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2.5 | 25 | 0.72
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 2.5 | 30 | 0.76
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3 | 10 | 0.34
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3 | 15 | 0.51
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3 | 20 | 0.64
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3 | 25 | 0.7
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3 | 30 | 0.75
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3.5 | 10 | 0.32
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3.5 | 15 | 0.5
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3.5 | 20 | 0.64
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3.5 | 25 | 0.7
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 3.5 | 30 | 0.75
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 4 | 10 | 0.31
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 4 | 15 | 0.51
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 4 | 20 | 0.65
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 4 | 25 | 0.72
A13H | A-13 | Exits | H | Rectangular | Pyramidal Diffuser at Fan Outlet without Difuser | [11 empty] | 4 | 30 | 0.76