## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | n, free area ratio | C
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | H (in) | W (in) | Q (cfm) | n, free area ratio | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.3 | 6.2
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | H (mm) | W (mm) | Q (m^3/hr) | n, free area ratio |  |  |  |  | 0.4 | 3
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.5 | 1.7
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.55 | 1.3
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.6 | 0.97
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.65 | 0.75
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.7 | 0.58
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.75 | 0.44
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.8 | 0.32
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 0.9 | 0.14
A14A2 | A-14 | Screens & Plates | A | Rectangular | Screen in Duct | [8 empty] | 1 | 0