## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | output 1 | output 2 | output 3 | output 4 | n, free area ratio | t/D | C
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | D (in) | Q (cfm) | n, free area ratio | plate thickness (in) | perforated hole diameter (in) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.2 | 0.015 | 52
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | D (mm) | Q (m^3/hr) | n, free area ratio | plate thickness (mm) | perforated hole diameter (mm) |  |  |  |  | 0.2 | 0.2 | 48
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.2 | 0.4 | 46
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.2 | 0.6 | 42
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.25 | 0.015 | 30
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.25 | 0.2 | 28
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.25 | 0.4 | 27
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.25 | 0.6 | 24
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.3 | 0.015 | 18
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.3 | 0.2 | 17
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.3 | 0.4 | 17
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.3 | 0.6 | 15
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.4 | 0.015 | 8.2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.4 | 0.2 | 7.7
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.4 | 0.4 | 7.4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.4 | 0.6 | 6.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.5 | 0.015 | 4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.5 | 0.2 | 3.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.5 | 0.4 | 3.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.5 | 0.6 | 3.2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.6 | 0.015 | 2
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.6 | 0.2 | 1.9
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.6 | 0.4 | 1.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.6 | 0.6 | 1.6
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.7 | 0.015 | 0.97
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.7 | 0.2 | 0.91
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.7 | 0.4 | 0.88
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.7 | 0.6 | 0.8
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.8 | 0.015 | 0.42
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.8 | 0.2 | 0.4
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.8 | 0.4 | 0.39
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.8 | 0.6 | 0.36
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.9 | 0.015 | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.9 | 0.2 | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.9 | 0.4 | 0.13
A14B1 | A-14 | Screens & Plates | B | Round | Perforated Plate in Duct, Thick | [9 empty] | 0.9 | 0.6 | 0.13