## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 3 | output 1 | output 2 | output 3 | output 4 | L/R | Ab/As | ANGLE | C
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | H (in) | W (in) | # blades - select from list | θ (degrees) | Q (cfm) | 1 | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.3 | 1 | 80 | 116
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | H (mm) | W (mm) | # blades - select from list | θ (degrees) | Q (m^3/hr) | 2 |  |  |  |  | 0.4 | 1.5 | 80 | 152
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [5 empty] | 3 |  |  |  |  | 0.5 | 0.3 | 80 | 188
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 80 | 245
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 80 | 284
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 80 | 361
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 80 | 576
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 70 | 32
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 70 | 38
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 70 | 45
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 70 | 45
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 70 | 55
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 70 | 65
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 70 | 102
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 60 | 14
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 60 | 16
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 60 | 18
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 60 | 21
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 60 | 22
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 60 | 24
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 60 | 28
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 50 | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 50 | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 50 | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 50 | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 50 | 9
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 50 | 10
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 50 | 10
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 40 | 5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 40 | 6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 40 | 6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 40 | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 40 | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 40 | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 40 | 5.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 30 | 2.3
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 30 | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 30 | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 30 | 2.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 30 | 2.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 30 | 2.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 30 | 2.7
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 20 | 1.4
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 20 | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 20 | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 20 | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 20 | 1.5
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 20 | 1.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 20 | 1.6
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 10 | 0.79
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 10 | 0.85
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 10 | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 10 | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 10 | 0.92
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 10 | 1
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 10 | 1
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.3 | 1 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.4 | 1.5 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.5 | 0.3 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.6 | 0.4 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 0.8 | 0.5 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1 | 0.6 | 0 | 0.52
A15E | A-15 | Obstructions | E | Rectangular | Damper, Parallel Blades | [10 empty] | 1.5 | 0.8 | 0 | 0.52