## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | L/H | C
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | H | W | B | Q (cfm) | Loss Coefficient | Fitting Loss (in w.c) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.5
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | H | W | B | Q (m^3/hr) |  |  |  |  | 1 | 0.86
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | [8 empty] | 1.5 | 0.83
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Single Blade Turning Vanes | [8 empty] | 2 | 0.77
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [8 empty] | 0.5
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [8 empty] | 1 | 1.85
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [8 empty] | 1.5 | 2.84
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, Double Blade Turning Vanes | [8 empty] | 2 | 2.91
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [8 empty] | 0.5 | 0.61
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [8 empty] | 1 | 0.65
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [8 empty] | 1.5
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, "S" type Splitter Vanes | [8 empty] | 2
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [8 empty] | 0.5 | 0.88
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [8 empty] | 1 | 5.26
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [8 empty] | 1.5 | 6.92
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Up to 1200 fpm (6 m/s) | [8 empty] | 2 | 7.56
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [8 empty] | 0.5 | 1.26
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [8 empty] | 1 | 6.22
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [8 empty] | 1.5 | 8.82
A15L | A-15 | Obstructions | L | Rectangular | Duct with 4-90° Mitered Ells to Avoid Obstruction, No Vanes - Over 1200 fpm (6 m/s) | [8 empty] | 2 | 9.24