## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 4 | dropdown 5 | output 1 | output 2 | output 3 | output 4 | curve ratio, CR | splitter vanes | R/W | H/W | Re | K | C
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | H (in) | W (in) | centerline radius (in) | # vanes - select from list | θ (degrees) | Q (cfm) | 1 | 30 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.218 | 1 | 0.05 | 0.25 | 10000 | 1.4 | 0.52
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | H (mm) | W (mm) | centerline radius (mm) | # vanes - select from list | θ (degrees) | Q (m^3/hr) | 2 | 45 |  |  |  |  | 0.302 | 1 | 0.1 | 0.25 | 20000 | 1.26 | 0.36
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [6 empty] | 3 | 60 |  |  |  |  | 0.361 | 1 | 0.15 | 0.25 | 30000 | 1.19 | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [7 empty] | 75 |  |  |  |  | 0.408 | 1 | 0.2 | 0.25 | 40000 | 1.14 | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [7 empty] | 90 |  |  |  |  | 0.447 | 1 | 0.25 | 0.25 | 60000 | 1.09 | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 0.25 | 80000 | 1.06 | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 0.25 | 100000 | 1.04 | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 0.25 | 140000 | 1 | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 0.25 | 200000 | 1 | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 0.25 | 10000 | 2 | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 0.25 | 20000 | 1.77 | 0.26
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 0.25 | 30000 | 1.64 | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 0.25 | 40000 | 1.56 | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 0.25 | 60000 | 1.46 | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 0.25 | 80000 | 1.38 | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 0.25 | 100000 | 1.3 | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 0.25 | 140000 | 1.15 | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 0.25 | 200000 | 1 | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 0.25 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 0.25 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 0.25 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 0.25 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 0.25 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 0.25 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 0.25 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 0.25 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 0.25 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 0.25 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 0.25 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 0.25 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 0.5 |  |  | 0.4
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 0.5 |  |  | 0.27
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 0.5 |  |  | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 0.5 |  |  | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 0.5 |  |  | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 0.5 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 0.5 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 0.5 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 0.5 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 0.5 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 0.5 |  |  | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 0.5 |  |  | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 0.5 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 0.5 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 0.5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 0.5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 0.5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 0.5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 0.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 0.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 0.5 |  |  | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 0.5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 0.5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 0.5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 0.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 0.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 0.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 0.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 0.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 0.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 1 |  |  | 0.43
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 1 |  |  | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 1 |  |  | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 1 |  |  | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 1 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 1 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 1 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 1 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 1 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 1 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 1 |  |  | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 1 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 1 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 1 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 1 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 1 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 1 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 1 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 1 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 1 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 1 |  |  | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 1 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 1 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 1 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 1 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 1 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 1 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 1 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 1 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 1 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 1.5 |  |  | 0.49
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 1.5 |  |  | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 1.5 |  |  | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 1.5 |  |  | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 1.5 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 1.5 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 1.5 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 1.5 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 1.5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 1.5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 1.5 |  |  | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 1.5 |  |  | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 1.5 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 1.5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 1.5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 1.5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 1.5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 1.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 1.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 1.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 1.5 |  |  | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 1.5 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 1.5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 1.5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 1.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 1.5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 1.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 1.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 1.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 1.5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 2 |  |  | 0.55
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 2 |  |  | 0.3
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 2 |  |  | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 2 |  |  | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 2 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 2 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 2 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 2 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 2 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 2 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 2 |  |  | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 2 |  |  | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 2 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 2 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 2 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 2 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 2 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 2 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 2 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 2 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 2 |  |  | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 2 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 2 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 2 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 2 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 2 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 2 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 2 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 2 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 2 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 3 |  |  | 0.66
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 3 |  |  | 0.35
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 3 |  |  | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 3 |  |  | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 3 |  |  | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 3 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 3 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 3 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 3 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 3 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 3 |  |  | 0.33
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 3 |  |  | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 3 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 3 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 3 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 3 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 3 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 3 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 3 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 3 | 0.05 | 3 |  |  | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 3 | 0.1 | 3 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.15 | 3 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.2 | 3 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.25 | 3 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.3 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.35 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.4 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.45 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.5 | 3 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 1 | 0.05 | 4 |  |  | 0.75
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 1 | 0.1 | 4 |  |  | 0.39
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 4 |  |  | 0.25
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 4 |  |  | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 4 |  |  | 0.13
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 4 |  |  | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 4 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 4 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 4 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 4 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 4 |  |  | 0.37
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 4 |  |  | 0.16
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 4 |  |  | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 4 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 4 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 4 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 4 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 4 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 4 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 4 |  |  | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 4 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 4 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 4 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 4 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 4 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 5 |  |  | 0.84
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 5 |  |  | 0.42
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 5 |  |  | 0.26
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 5 |  |  | 0.18
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 5 |  |  | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 5 |  |  | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 5 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 5 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 5 |  |  | 0.41
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 5 |  |  | 0.17
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 5 |  |  | 0.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 5 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 5 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 5 |  |  | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 5 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 5 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 5 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 5 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 5 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 6 |  |  | 0.93
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 6 |  |  | 0.46
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 6 |  |  | 0.28
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 6 |  |  | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 6 |  |  | 0.14
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 6 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 6 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 6 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 6 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 6 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 6 |  |  | 0.45
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 6 |  |  | 0.19
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 6 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 6 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 6 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 6 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 6 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 6 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 6 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 6 |  |  | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 6 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 6 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 6 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 6 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 6 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 7 |  |  | 1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 7 |  |  | 0.49
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 7 |  |  | 0.3
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 7 |  |  | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 7 |  |  | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 7 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 7 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 7 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 7 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 7 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 7 |  |  | 0.48
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 7 |  |  | 0.2
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 7 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 7 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 7 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 7 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 7 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 7 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 7 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 7 |  |  | 0.22
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 7 |  |  | 0.08
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 7 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 7 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 7 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 7 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.218 | 1 | 0.05 | 8 |  |  | 1.1
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.302 | 1 | 0.1 | 8 |  |  | 0.52
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.361 | 1 | 0.15 | 8 |  |  | 0.32
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.408 | 1 | 0.2 | 8 |  |  | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.447 | 1 | 0.25 | 8 |  |  | 0.15
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.48 | 1 | 0.3 | 8 |  |  | 0.12
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.509 | 1 | 0.35 | 8 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.535 | 1 | 0.4 | 8 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.557 | 1 | 0.45 | 8 |  |  | 0.06
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.577 | 1 | 0.5 | 8 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.362 | 2 | 0.05 | 8 |  |  | 0.51
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.45 | 2 | 0.1 | 8 |  |  | 0.21
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.507 | 2 | 0.15 | 8 |  |  | 0.11
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.55 | 2 | 0.2 | 8 |  |  | 0.07
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.585 | 2 | 0.25 | 8 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.613 | 2 | 0.3 | 8 |  |  | 0.04
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.638 | 2 | 0.35 | 8 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.659 | 2 | 0.4 | 8 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.677 | 2 | 0.45 | 8 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 2 | 0.5 | 8 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.467 | 3 | 0.05 | 8 |  |  | 0.23
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.549 | 3 | 0.1 | 8 |  |  | 0.09
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.601 | 3 | 0.15 | 8 |  |  | 0.05
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.639 | 3 | 0.2 | 8 |  |  | 0.03
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.669 | 3 | 0.25 | 8 |  |  | 0.02
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.693 | 3 | 0.3 | 8 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.714 | 3 | 0.35 | 8 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.731 | 3 | 0.4 | 8 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.746 | 3 | 0.45 | 8 |  |  | 0.01
A7G | A-7 | Elbow | G | Rectangular | Smooth Radius with Splitter Vanes | [12 empty] | 0.76 | 3 | 0.5 | 8 |  |  | 0.01