## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | dropdown 4 | output 1 | output 2 | output 3 | output 4 | A1/A | ANGLE | C
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | H (in) | H₁ (in) | W (in) | θ (degrees) - select from list | Q (cfm) | 10 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 1.5 | 10 | 0.05
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | H (mm) | H₁ (mm) | W (mm) | θ (degrees) - select from list | Q (m^3/hr) | 15 |  |  |  |  | 1.5 | 15 | 0.06
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [5 empty] | 20 |  |  |  |  | 1.5 | 20 | 0.07
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [5 empty] | 25 |  |  |  |  | 1.5 | 25 | 0.09
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [5 empty] | 30 |  |  |  |  | 1.5 | 30 | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [5 empty] | 35 |  |  |  |  | 1.5 | 35 | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 10 | 0.08
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 15 | 0.1
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 20 | 0.11
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 25 | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 30 | 0.18
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2 | 35 | 0.23
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 10 | 0.11
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 15 | 0.12
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 20 | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 25 | 0.18
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 30 | 0.23
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 2.5 | 35 | 0.28
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 10 | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 15 | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 20 | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 25 | 0.2
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 30 | 0.26
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3 | 35 | 0.33
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 10 | 0.13
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 15 | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 20 | 0.16
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 25 | 0.21
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 30 | 0.28
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 3.5 | 35 | 0.35
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 10 | 0.14
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 15 | 0.15
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 20 | 0.16
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 25 | 0.22
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 30 | 0.29
A8I | A-8 | Transition (Diverging Flow) | I | Rectangular | Asymmetric at Fan with Sides Straight, Top 10° Up | [10 empty] | 4 | 35 | 0.36