## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | dropdown 5 | output 1 | output 2 | output 3 | output 4 | A1/A | ANGLE | C
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | H (in) | W (in) | H₁ (in) | W₁ (in) | θ (degrees) - select from list | Q (cfm) | 10 | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 1.5 | 10 | 0.1
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | θ (degrees) - select from list | Q (m^3/hr) | 15 |  |  |  |  | 1.5 | 15 | 0.23
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [6 empty] | 20 |  |  |  |  | 1.5 | 20 | 0.31
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [6 empty] | 25 |  |  |  |  | 1.5 | 25 | 0.36
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [6 empty] | 30 |  |  |  |  | 1.5 | 30 | 0.42
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2 | 10 | 0.18
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2 | 15 | 0.33
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2 | 20 | 0.43
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2 | 25 | 0.49
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2 | 30 | 0.53
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2.5 | 10 | 0.21
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2.5 | 15 | 0.38
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2.5 | 20 | 0.48
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2.5 | 25 | 0.55
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 2.5 | 30 | 0.59
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3 | 10 | 0.23
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3 | 15 | 0.4
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3 | 20 | 0.53
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3 | 25 | 0.58
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3 | 30 | 0.64
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3.5 | 10 | 0.24
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3.5 | 15 | 0.42
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3.5 | 20 | 0.56
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3.5 | 25 | 0.62
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 3.5 | 30 | 0.67
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 4 | 10 | 0.25
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 4 | 15 | 0.44
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 4 | 20 | 0.58
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 4 | 25 | 0.64
A8J | A-8 | Transition (Diverging Flow) | J | Rectangular | Pyramidal at Fan with Duct | [11 empty] | 4 | 30 | 0.69