## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | input 5 | input 6 | input 7 | output 1 | output 2 | output 3 | output 4 | L/D | A/A1 | ANGLE | K | C
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | H (in) | W (in) | H₁ (in) | W₁ (in) | L (in) | θ (degrees) | Q (cfm) | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 0.025 | 0 | 0 | 1 | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | H (mm) | W (mm) | H₁ (mm) | W₁ (mm) | L (mm) | θ (degrees) | Q (m^3/hr) |  |  |  |  | 0.025 | 0.2 | 10 | 0.85 | 0.47
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 | 0.4 | 20 | 0.68 | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 | 0.8 | 30 | 0.5 | 0.43
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 | 0.8 | 40 | 0.3 | 0.41
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 | 0.9 | 60 | 0.18 | 0.4
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 | 1 | 100 | 0 | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 |  | 140 |  | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.025 |  | 180 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 0 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 10 |  | 0.45
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 20 |  | 0.41
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 30 |  | 0.36
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 40 |  | 0.33
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 60 |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 100 |  | 0.35
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 140 |  | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.05 |  | 180 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 0 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 10 |  | 0.42
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 20 |  | 0.35
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 30 |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 40 |  | 0.26
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 60 |  | 0.23
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 100 |  | 0.3
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 140 |  | 0.4
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.075 |  | 180 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 0 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 10 |  | 0.39
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 20 |  | 0.32
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 30 |  | 0.25
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 40 |  | 0.22
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 60 |  | 0.18
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 100 |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 140 |  | 0.38
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.1 |  | 180 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 0 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 10 |  | 0.37
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 20 |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 30 |  | 0.2
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 40 |  | 0.16
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 60 |  | 0.15
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 100 |  | 0.25
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 140 |  | 0.37
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.15 |  | 180 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 0 |  | 0.5
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 10 |  | 0.27
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 20 |  | 0.18
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 30 |  | 0.13
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 40 |  | 0.11
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 60 |  | 0.12
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 100 |  | 0.23
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 140 |  | 0.36
A9B2 | A-9 | Transition (Converging Flow) | B | Rectangular | Stepped Pyramidal Contraction | [11 empty] | 0.6 |  | 180 |  | 0.5