## Sheet1
ID | FITTING | FITTING TYPE | FITTING LETTER | SHAPE | NAME | input 1 | input 2 | input 3 | input 4 | output 1 | output 2 | output 3 | output 4 | Re | R_e | C
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | D (in) | H₁ (in) | W₁ (in) | Q (cfm) | Loss Coefficient | Fitting Loss (in w.c.) | Velocity (Vₒ, fpm) | Vel Pres. at Vₒ (Pv, in. wc) | 10000 | 1*10^4 | 0.27
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | D (mm) | H₁ (mm) | W₁ (mm) | Q (m^3/hr) |  |  |  |  | 20000 | 2*10^4 | 0.25
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 40000 | 4*10^4 | 0.2
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 60000 | 6*10^4 | 0.17
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 80000 | 8*10^4 | 0.14
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 100000 | 10*10^4 | 0.11
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 200000 | 20*10^4 | 0.04
A9C | A-9 | Transition (Converging Flow) | C | Rectangular | Rectangular Slot to Round | [8 empty] | 400000 | >=40*10^4 | 0